DYNAMIC PERFORMANCE ENHANCEMENT

OF

POWER SYSTEM USING STATIC VAR SYSTEM

A DISSERTATION

Submitted in partial fulfilment of the requirements for the award

MASTER OF ENGINEERING IN

ELECTRICAL ENGINEERING (CONTROL & INSTRUMENTATION)

Under the guidance of

Dr. Narendra Kumar

Professor

Submitted By:

AJENDRA SINGH

University Roll No-12612

DEPARTMENT OF ELECTRICAL ENGINEERING,

DELHI COLLEGE OF ENGINEERING

UNIVERSITY OF DELHI

INDIA

CERTIFICATE

Dynamic Performance Enhancement of POWER SYSTEM using Static VAR System is a dissertation work submitted in partial fulfilment of the requirement for the award of degree in Master of Engineering (CONTROL& INSTRUMENTATION) in Delhi College of Engineering, University of Delhi by him. He has worked for this dissertation under my guidance and the work has not been submitted elsewhere for the award of a degree.

(PROF. NARENDRA KUMAR)

ACKNOWLEDGEMENT

I express my foremost and deepest gratitude to Prof. Narendra Kumar and Prof. S.T.Nagarajan in the Department of Electrical Engineering, Delhi College of Engineering and University of Delhi for his guidance, support and encouragement throughout my dissertation. I consider myself fortunate for having the opportunity to learn and work under his able supervision and guidance over the entire period of association with him. I have deep sense of admiration for his innate goodness. I can offer my profound indebtedness to him for his deep concern for my academics. My sincere thanks are due to Prof. Pramod Kumar for his support, encouragement and time to time invaluable guidance.

Lastly my deepest gratitude is due to Almighty God whose divine light provided me the perseverance, guidance, inspiration and strength to complete this work.

AJENDRA   SINGH

ABSTRACT

Flexible Alternating current transmission system (FACTS) devices are used widely for the dynamic control of voltage, impedance and phase angle of high voltage AC lines. Thus with FACTS controllers the existing transmission facility can be fully utilized and hence minimizing the gap between stability limit and thermal stability. Many preventive measures to cope with dynamic instability problem in series compensated lines have been reported in literature [1]. Among these the application of Static Var Systems (SVS) controller has gained the importance in recent years in modern power systems due to its capability to work as Var generator and absorption systems [2, 3, and 4]. Besides voltage control and improvement of transmission capability SVS in coordination with auxiliary signals can be used for damping of power system oscillations effectively [5, 6]. The selection of location of an effective location and feedback signal is an important aspect to employ FACTS controllers [7].It is often seen that the control of SVS has not been demonstrated over a wide operating range [8, 9]. It requires an effective SVS controller to be developed which is applicable over a wide operating range and under large disturbance conditions.

A detailed system model which can reflect system dynamics accurately over a wide operating range has to be developed. Proper location of SVS and Series compensation play a very important role for enhancement of dynamic and transient stability of power system [11]. Thus there is need to determine the optimal location of static var system and the amount of series compensation in the power systems. Also the rating of SVS should be based on steady state analysis because SVS may cause high power transfer level over long distance.

Different types of SVS auxiliary signals and their combination have been tried to find out the most effective auxiliary signal or effective combination for enhancement of dynamic and transient performance over a wide operating range.

A detailed system model has been developed for the dynamic and transient performance of the system (Chapter -2). The study system consists of a generator supplying power to an infinite bus over a long transmission line. In the detailed machine model, the stator is represented by a dependent current source in parallel with the inductance. Its rotor flux linkage is expressed in terms of currents which are defined wit respect to the machine reference frame. To have a common axis of representation with the network and SVS, these flux linkages are transformed to synchronously rotating D-Q frame of reference

A SVS auxiliary controller is then developed using Matlab, which is advanced software for analyzing and simulating a variety of dynamic systems. The performance is evaluated for enhancement of dynamic stability of a series compensated transmission lines by computing the Eigen value of the linearised system model. The dynamic performance of the series compensated power system has been evaluated by performing the Eigen value analysis .A linearised power system model has been developed and system Eigen values have been computed with and without incorporating the combined reactive power and voltage angle SVS auxiliary controller. It is seen that the unstable modes of the system are effectively stabilized and the dynamic performance is greatly improved.

CONTENTS

Chapter-I Introduction  						10-14

1.1 Static Var System

1.2 Application of Static Var Systems

1.3 Dissection of Dissertation

Chapter-2 Literature Review 					15-17

2.1 Application of Static Var systems

2.2 Dynamic performance enhancement

Chapter-3  Modelling of power systems 		18-44

3.1 Introduction

3.2 System Model

3.2. Network Model

3.3 Static VAR system Model

3.5 Development of the System Model

Chapter-4 AUXILIARY CONTROL OF SVS  		45-51

4.1 Introduction

4.2 Auxiliary controller Design

4.3 System Model with Auxiliary controller

Chapter-5 CASE STUDY						52-56

5.1 Case Study

5.2 Dynamic Performance

5.3 Eigen Values with or without auxiliary controller

Chapter-6 Conclusions 						57-58

6.1 General

Chapter 7 								59

7.1 Scope for future work

References  								60-62

Appendix									63-71

Appendix A1

Appendix A2

Appendix A3

# LIST OF SYMBOLS

B		Susceptance

D		Damping Constant

E, e		Source Voltage

F0		Nominal system frequency

G		Conductance

I,I		Current

J		−1

K		Spring Constant

KP		Proportional gain of SVS voltage controller

KI		Integral gain of SVS voltage controller

KB		Gain of SVS auxiliary controller

KD		Slope of SVS control characteristics

L		Inductance

M		Inertia constant

P		Real power

Q		Reactive power

R,r		Resistance

S		Complex power

Te		Electrical torque

Tm		Mechanical torque

Ts		firing delay time constant

TD		Thyristor dead time constant

TM		Measurement time constant

t		Time in seconds

u		Input variable

V		Voltage

X		Reactance

Y		Admittance

Z		Impedance

Greek Symbols

δ		Generator rotor angle

ψ		Flux linkage

θ		angle

ω		Angular velocity (rad/sec)

Prefix

Δ		Incremental Change

Superscripts

t		Transpose

Subscripts

R,M,E,N	Rotor circuit, Mechanical, Excitation System, Network

C		SVS auxiliary controller

G,g		Generator

α, β, 0		α- β- 0 axis variables

d,q,0		d-q-o	axis variables

D, Q, 0		D- Q_0 axis variables

- Initial value

F, g, h, k	field and other rotor coils

A dot over a symbol indicates differential with respect to time.

The other symbols used in the text are explained as and when they are introduced.

CHAPTER 1

INTRODUCTION

In recent years, dynamic stability has become one of the most important problems in power system operation. Therefore, significant research efforts have been devoted in developing new analysis tools to cope with this type of stability.

Due to environmental, regulatory and economical constraints, modern power systems are been forced to operate closer to their load ability limits. This has a negative effect on the stability of the system. Hence there is a need to increase the capabilities of transmission lines, the increase in generation near the load centre, the reduction in cyclic peak load requirements, etc. However these methods are either costly or difficult to implement.

FACTS devices are very effective and capable of enhancing the power transfer capability and flexible control of power flow through transmission lines while maintaining stability and reliability of power system [12].

IEEE has given the definition of FACTS as follows-

“Alternating current transmission systems incorporating power electronics based and other static controllers to enhance controllability and increase power transfer capability.”

The FACTS technology is not a single high power controller but rather a collection of controllers which can be applied individually or in coordination with other to control one or more of the inter related system parameters like voltage, current, impedance, phase angle and system parameters like voltage, current, impedance, phase angle and damping of oscillations at various frequencies below the rated frequency.

The Facts controllers can be classified according to their connection to the controlled AC Transmission system as-

1. Shunt connected controllers

2. Series connected controllers

3. Combined shunt and series connected controllers

4. Combined series-series controllers.

1.1 Static Var System (SVS)

SVS are used to control the voltage profile under load variations, increase power transfer capability and to improve system stability. They can be used for damping power system oscillations incorporating some auxiliary signals. SVC’s are first generation FACTS controllers which are expected to revolutionaries’ power transmission in future. These are also used for power factor compensation of dynamic loads such as steel mills and arc furnaces and load balancing. They can provide better control of power flow on parallel path which is important in relatively tight mesh networks [14].

There are mainly two types of Static VAR Compensator configuration which are used in power system. A continuous control over the capacitive and inductive range of reactive power can be achieved from either of two SVS configurations, FC-TCR or TSC-TCR.[13].

It has been reported by Gyugyi [13] that while the steady state characteristics and response of both the compensators are identical for small voltage perturbations, the operating behaviour of TSC-TCR is also characterized by low losses and reduced harmonic contents.

1.2 Applications of Static VAR Compensators:

By virtue of the ability of SVC to provide continuous and rapid control of reactive power and voltage SVS can enhance many aspects of transmission system performance. Applications to date include the following-

􀂉Control of temporary over voltages

􀂉Prevention of voltage collapse

􀂉Enhancement of Transient Stability

􀂉Enhancement of damping of system oscillation

􀂉Balancing the unbalanced loads

􀂉Eliminating voltage flicker

􀂉Damping sub-synchronous resonance

􀂉Power factor improvement

􀂉Loss reduction

􀂉Enhancement of power transfer capability

STATCOM, Static Synchronous Compensator belongs to the second generation FACTS controller and is based on voltage source converter using gate turn off thyristors (GTO’s) and is presently considered the most practical for high power utility applications. The controller can provide both capacitive and inductive compensation and is able to control output current over the rated maximum capacitive or inductive range independent of AC System voltage. The controller can provide full capacitive output current at any output current with the decreasing system voltage.

So STATCOM is more effective than the SVC for voltage improvement and transient stability enhancement.

SSSC, Static Synchronous Series Compensator was proposed by Gyugyi in 1989. It is a Static Synchronous Series generator operated without an external electric energy source as a series compensator whose output voltage is in quadrature with and controllable independently of the line current for increasing or decreasing the overall reactive voltage drop across the line and thereby controlling the transmitted electric power. It is like STATCOM, except the output AC voltage is in series with the line.

1.3 Dissection of Dissertation

A chapter wise summary of the work done in this dissertation is described below-

Chapter 1 describes the introduction part of the dissertation highlighting the development of the system model for dynamic performance of the system. Study system consists of a generator supplying power to an infinite bus over a long transmission line. In the detailed machine model, the stator is represented by a dependent current source in parallel with the inductance. Its rotor flux linkage is expressed in terms of currents which are defined wit respect to the machine reference frame. To have a common axis of representation with the network and SVS, these flux linkages are transformed to synchronously rotating D-Q frame of reference.

The generator model includes field winding and a damper winding along q-axis.

The network is represented by using π circuit .The midpoint location of the SVS is chosen with regards to its capability to transfer maximum power over the line.

In chapter 2, a new scheme has been developed for achieving stability in transmission lines. The scheme utilizes the damping effect of combined reactive power and voltage angle SVS auxiliary controller.

Chapter 3 There are the modelling of power systems which has different model in developed form and their details

Chapter 4 A Case study of dynamic performance enhancement of power system using SVS with and without Auxiliary controller.

Chapter 5 The dynamic performance of the series compensated power system has been evaluated by performing the eigen value analysis .A linearised power system model has been developed and system eigen values have been computed with and without incorporating the combined reactive power and voltage angle SVS auxiliary controller. It is seen that the unstable modes of the system are effectively stabilized and the dynamic performance is greatly improved.

Chapter 6 includes Results and conclusion with Eigen values are calculated by MATLAB.

CHAPTER 2

LITERATURE REVIEW

A Detailed literature survey shows that there has been a lot of work done in the field of FACTS controller, especially Static VAR System and there is a great need to improve the reactive power control strategy.

2.1 Application of Static Var Systems

The application of SVS in long distance power system has received much attention by researchers in recent years. By virtue of its ability to provide continuous and rapid control of reactive power and voltage, SVS can enhance several aspects of transmission system performance. The work reported in literature in the area of SVS application has been classified as follows-

2.2 SVS for Dynamic Performance Enhancement

Static Var System is known to extend the stability limit and improve system damping when connected at the intermediate points of the transmission line.

Nelson Martins and L.T.G Lima [15] presented the work relating to the location of SVC taking into account various factors such as dynamic voltage support, capability of damping electromechanical and sub synchronous oscillations. The proposed algorithm attempted to provide an answer to the problems of finding the best location for the sole purpose of damping electromechanical oscillations.

K.R.Padiyar and R.K.Varma [16] presented work concerned with application of damping torque technique to examine the efficacy of various control signals for reactive power modulation of a midpoint located SVS in enhancing power transfer capability of long transmission line.

A new auxiliary signal designated as computers inter frequency [5] was proposed.

Shun Lee and Chun Chang Liu [17] investigated an output feedback SVC for damping the electromechanical oscillations of synchronous generator. An Eigen structure assignment technique was applied to design the controller. Eigen value analysis and time domain simulation under different loading conditions were performed in order to demonstrate the effectiveness of the proposed controller.

E.Lerch etal [18] presented an advanced SVC control for damping power oscillations. The proposed SVC used phase angle signal estimated from the measurement of voltage and power at SVC location. As a result of this method it is possible to increase the power system damping considerably particular in critical situations near to stability limit.

E.Z. Zhou [19] developed a theory to analyze power system damping enhancement by application of SVS based on the well known equal criteria. A discontinuous SVC control approach was proposed in which the change of reactive power output at discrete power points was determined by the power deviation on a transmission line. The author proposed that the SVC control approach and developed theory could be applied to solve practical power system damping problems.

K.Ramar and A.Srinivas [3] developed a linearized model of a single machine infinite bus system with SVC for low frequency oscillation studies. Norouzi, A.H and Sharaf, A.M in their paper on two control schemes to enhance the dynamic performance of the STATCOM and SSSC have done an in-depth investigation of the dynamic performance of the Static Synchronous Compensator (STATCOM) and the Static Synchronous Series Compensator (SSSC) theoretically and by exact digital simulation. A 24-pulse GTO dc-ac converter model is designed to represent the operation of the STATCOM and SSSC within a power transmission system.

Two major factors of the STATCOM instability are analyzed and a new Automatic Gain Controller (AGC) is proposed to ensure the stable operation of the STATCOM under various load conditions.

Pourbeik, P. and Bostrom, A.Ray, B. present a description of modelling and application studies related to a modern static VAR system (SVS) installation in a utility grid. The SVS incorporates a fully integrated static Var compensator (SVC) and coordinated, automatically switched capacitor banks using a sophisticated control system. The capacitor banks are switched by individual circuit breakers. Descriptions are provided for the SVC control strategy and various levels of modelling details for the application and design studies performed for this device. S.Lefebvre etal [20] presented an SVC model based on modal analysis. The model was integrated in EMTP with minimal interface error and by taking into account initialization.

Rahim[21] etal proposed a coordination of dynamic braking strategy and excitation control to arrest the first swing stability as well as subsequent oscillations in power systems. Computer simulation of multimachine system showed a coordinated application of braking resistor capacitor and excitation energy controls the transients effectively.

A.S.R Murthy etal [22] has an attempted to use deviation of reactive power as auxiliary control signal for SVS. The auxiliary controller parameters were obtained using Eigen value analysis and by employing the criterion that the damping factor of the two sensitive Eigen values was made nearly equal.

CHAPTR 3

MODELLING OF POWER SYSTEM

3.1 INTRODUCTION

High power electronic devices are bringing unprecedented increases in efficiency and cost-effectiveness in electrical power systems.  Moreover, the operational flexibility they introduce will enable utilities to significantly increase asset utilization and deliver new value-added customer services. Flexible AC Transmission System (FACTS) [l] devices and other complementary technologies can minimize costly capital investments, but evaluating and selecting the appropriate devices is a complex task. Power system planners need a way to identify the optimal FACTS solution for maximizing system capabilities.

Static VAR system is a FACTS device that besides controlling the power flow, voltage profile under load variations, increasing power transfer capability and stability of the system, improves damping power system oscillations incorporating some auxiliary signals.

An efficient design of SVS controller must consider the appropriate model of system and the SVS. The knowledge of adequate system model is essential for predicting the exact system behavior and SVS performance under abnormal conditions. In the literature the SVS and system models repeatedly vary from the most simplistic representation of both AC system and SVS [8, 23] to detailed representation of generator, network and SVS [24,25]. However the higher order system models are useful for assessing the dynamic stability and transient stability.

A detailed system model is developed for the study system consisting of a generator supplying power to an infinite bus over a long distance transmission line. The SVS is located at the middle of transmission line. The system model is developed using a network model represented by single lumped parameter ∏ network model. The dynamic performance of the system has evaluated using the two system models of AC networks and the results are compared over the wide operating range. The studies performed can be categorized as follows.

1. The method of Eigen value analysis is employed to assess the dynamic behavior of the system and the unstable system modes are investigated

2.The line reactive power controllers have been developed and incorporated in the SVS control systems as a result the unstable systems mode are stabilize over a wide operating range.

3. The dynamic performance of the system has been evaluated using the network models represented by the single lumped parameter ∏ circuit on either side of SVS and the results are compared over a wide operating range.

3.2 System Model

3.2.1 System Description-

The study system consists of a generating station supplying bulk power to a large power system over a long distance transmission line. SVS is located at the center of transmission line. The generating station is represented by an equivalent synchronous generator and the large power system is represented as an infinite bus. The single line diagram of the study system is shown in fig 3.1. The SVS is assumed to be of switched capacitor thyristor controlled reactor

Type configuration and is connected to transmission network through a coupling transformer. The study system can be divided into three sub systems for modeling point of view.

Fig.3.1 Study System

- Generator Model

The detailed mathematical model of synchronous generator used here is in such from which can be directly utilized for dynamic stability analysis and system simulation. The synchronous generator is represented by three symmetrically placed armature windings a, b, c, one field winding ‘f’ and three damper windings ‘h, g, k’, (fig.3.2). The damper windings are considered to model the eddy current effects in a solid rotor machine. The following assumptions are used in deriving the basic equations of the machine.

- The m.m.f. is distributed sinusoidal in the air gap and harmonies are neglected.

- Sub transient saliency is neglected, Xd} } } {=Xq} } } {

- The effects of machine damping and prime mover dynamics are small and hence neglected for simplicity.

- Magnetic saturation and hysteresis are neglected.

The synchronous generator model can be divided in following subsections as:

    - Stator

(b)	Rotor

(c)	Mechanical system

(d)	Excitation System

- Stator: - In the detailed machine model the stator of synchronous generator in represented by a constant Current source parallel with constant inductance L

Fig. 3.2 Schematic layout of windings of synchronous machine and their two axis representation

The above model simplifies the problem of interfacing the machine and network which is required for solution of synchronous machine equations along with network equations. The dependent current source replaces the time varying coupling between the stator windings and rotor winding. Is is a (3x6) vector and LS} } } { is a (3x3) matrix. These are expressed as:

Is = [Ia Ib Ic]t  = IdC + IqS 								(3.1)

Where:

Id = C1ψf + C2ψhIq= C3ψg + C4ψk + C5ψc

Id and Iq are the component of dependant current source along d and q axis respectively.

θ = rotor angle

The contrast C6- C5 are given in appliance A,

LS} } `=` {  {L rSub { size 8{0} } }  over  {3} } ` left [ matrix {
1 {} # 1 {} # 1 {} ##
1 {} # 1 {} # 1 {} ##
1 {} # 1 {} # 1{}
}  right ]`+` {  {2L rSub { size 8{d} }  rSup { size 8{3 1−12−12−121−12−12−121        					(3.2)

Where Ld} } } { = Sub transient inductance of machine

Lo = zero sequence inductance of machine

Such a representation of machine can handle both the symmetrical and unsymmetrical network equally well. If the external network connected to machine terminal is symmetrical, as considered in this case a, b, c components can be transformed to , , o components by using Clarke’s transformation. All the three ,,o component models are uncoupled. Moreover  network is identical with  network and is same as positive sequence network model. Equivalent source representation of the machine on , o axis is shown in fig. (2.3). the equivalent circuit consists of three meshes which are not mutually coupled. The currents in the meshes correspond to , o components of armature currents. The relationship between , o component and phase currents IA, IB, IC given by

lalblc = 23013−16−1213−161213 lαlβl0                                     	           (3.3)

The dependent current sources in , o frame of reference are defined as

l = Id cos θ + IQ sin θ								(3.4)

l =- Id sin θ+ IQ cos θ  								(3.5)

Io = 0

The -axis equivalent representation of the machine stator current can be directly combined with  network of the AC transmission system.

(ii)	Rotor

The rotor flux linkages are defined as follows

ψf.=a1ψf+a2ψh+b1Vf+b2Idψh.=a3ψf+a4ψh+b3Idψg.=a5ψg+a6ψk+b5Iqψk.=a7ψg+a8ψh+b6Iq						(3.6)

Where VT is field excitation voltage

Fig.3.3 Equivalent Representation of Synchronous Machine on , o

Constants a1 to a8 and b1 to b6 are defined in appendix A1,  and  are the   d-axis and q- axis components of the machine terminal currents and are defined by

ld = 23 iacosθ + ib cos θ−2π3 + ic cos θ+2π3 				(3.7)

lq = 23 ia sin θ + ibsin θ−2π3 + ic sin θ+2π3  				(3.8)

It is noted that currents ld and lq are defined w. r. t. machine reference frame. These currents are transformed to D-Q frame of reference to have common of representation with the AC network and SVS which is rotating at synchronous speed wo. The following transformation is employed.

ldlq = cos δ−sin δsin δcos δ lDlQ   							(3.9)

Where lD, lQ, are the competent of the machine current along D-axis and Q-axis respectively. Substituting equation (3.9) in equation (3.1) linearizing the resultant equations. We have the state equation of the rotor circuit as following

+ b2cos δ−b2sin δb3cosδ−b3sinδb5sinδb5cos δb6sinδb6cosδ ΔidΔig

Or

XR.=ARXR+BR1UR1+BR2UR2+BR3UR3					  (3.10)

Where XR = [f  h  g k]t

uR1 = [  ω]t , uR2 = [vf]t, uR3 = [iD   iQ]t

The output equations of rotor circuit are developed by using the relationship between Id, Iq, and rotor flux linkages

Id = C1f + C2h

Iq = C3g + C4k									(3.11)

Where Id and Iq are the components of the dependant current sources shown along d and q axis respectively

C1 = Xdf Xh − Xdh XfhXd} } ` \( X rSub { size 8{f} } X rSub { size 8{h} } '` - `X rSub { size 8{ ital fh} }  rSup {2}  size 12{ \) }} } ,````C rSub {2}  size 12{`=` {  {X rSub { ital dh}  size 12{X rSub {f} } size 12{` - `X rSub { ital fh} } size 12{`X rSub { ital df} }}  over  { size 12{X rSub {d  rSup { (XfXh−Xfh2)

C3 = Xqg Xk − Xqk XgkXd} } ` \( X rSub { size 8{g} } X rSub { size 8{k} }  - X rSub { size 8{ ital qk} }  rSup { size 8{2} }  \) } } `,```C rSub { size 8{4} } `=` {  {X rSub { size 8{ ital qk} } `X rSub { size 8{g} }  - X rSub { size 8{ ital gk} } `X rSub { size 8{ ital qg} } }  over  {X rSub { size 8{d} }  rSup { size 8{ (XgXk−Xgk2)

By kron’s transformation

IDIQ = cos δsin δ−sin δcos δ IdIq							(3.12)

Or ID = (C6 f + C2h) cos  + (C3g+C4k) sin 

And   IQ = - (C6 f + C2h)sin  + (c3g+c4k) cos   				(3.13)

Linearizing Equation (3.13) we get

ΔI.DΔI.G = C1 cos δC2cos δC3 sin δC4 sin δ−C1sin δ−C2sin δC3 cos δC4 cos δ ΔψfΔψhΔψgΔψk	+ IQ00−ID00 ΔδΔw

Or YRI = [CR6] XR + [DR6] UR6							(3.14)

By differentiating and linearizing Equation (3.13)

ΔI.DΔI.Q = (C1a1 + C2a3)(C1a2+C2a)4(C3a5+C4a7)(C3a6+C4a8)cos δcos δsin δsin δ−(C1a 1+C2a2)−(C1a3+C2a4)(C3a5+C4a7)(C3a6+C4a8)sin δsin δcos δcos δ

x ΔψfΔψhΔψgΔψk + −(C1b2+C2b3) id0 cos δ0lQ0+(C3b5+C4b5)id0 sin δ0(C1C2+C2b3)iq0sinδ0+(C3b5+C4b6) iq0cosδ0−lD0 ΔδDΔωD

+ C1b1cosδ0−C1b1sinδ0 ΔVf

+ (C1b2+C2b3) cos2δ0−(C1b2+C2b3) sin δ0 cos δ0+ (C3b5+ C4b6) sin2δ0+ (C3b5+C4b6) sin δ0 cos δ0−(C1b1+C2b3) sin δ0cosδ0(C1b2 + C2b3) sin2δ0+(C3b5+C4b6) sin δ0cosδ0+(C3b5+C4b6) cos2δ0 ΔlDΔlQ

Where ldo = lDO cos o - lQ0 sin o

Lqo = lD0 sin o - lD0 cos o

IDO = (C6f + C2h) cos o + (C3g + C4k) sin o

IQO = - (C6f + C2h) sin o + (C3g + C4k) cos o

Or YR2 = [CR2] X R + [DR2] uR6 + [DR3] uR2 + [DR4] uR3	                   		 (3.15)

(iii)	Mechanical System

The rotor angle is expressed as :

(3.16)

Where

The Nominal system frequency  is given by

(3.17)

Differentiating equation 3.16 and substituting equation 3.17

Or

Or   									(3.18)

The machine swing equation is given by

(3.19)

Where

H=inertia constant of the system

D= damping torque co-efficient

=Mechanical Torque

=Electrical torque

The electromagnetic torque  is given by

(3.20)

Substituting equation (3.20) is equation (3.19)

(3.21)

, and  ,  are  transformed to D-Q frame of refrence using the relationship given by equation (3.9)

(3.22)

Linearizing equation (3.18) and (3.22) and writing in matrix form we have

(3.23)

Where

Or

(3.24)

Where

The output equation of the mechanical sub system is given by

Or 					      (3.24)

(iv)	Excitation System:

The excitation system is represented by the IEEE type – 1 model [26] as shown in fig (3.5) Vg represents the generator terminal voltage and SE is the saturation function. The excitation system is described by the following equations

Fig. 3.4 IEEE Type 1 Excitation System

V.f = −(KE + SE)TE Vf + 1TE Vr

V.S = −KF(KE+SE)TETFVf−1TE VS+KFTETFVr						(3.26)

V.r= −KATAVS −1TAVr − KATAVg + KATA VREF

The state and out put equations of the linearized system are

ΔV.fΔV.sΔV.r = −(KE+SE)TE01TE−KF(KE+SE)TETF−1TFKFTETF0−KATA−1TA ΔVfΔVsΔVr + 00−KATA

Or XE. = [AE] XE + [BE] UE 								(3.27)

The out put equation in given by

ΔVf = 1 0 0 ΔVfΔVsΔVr

Or   YE = [CE] XE									(3.28)

Where XE = [Vf Vs Vr] t UE = Vg, YE = Vf

3.3 Network Model

Π –Circuit Representation

The  dynamic performance of the network model represented by the lumped parameter ∏ circuit is compare with the network model using single lumped parameter π circuit on either side SVS. Fig3.5.

Fig.3.5 α-axis representation of AC network (∏ Circuit)

The governing equation along the – axis for the π- network representation can be derived as follows.

(3.29)

(3.30)

Where

LA=LT1+Ld} } } {	 And

Similarly the equation can be derived for the β- network. α- β network equation are then transformed to D-Q frame of reference using the transformation given by the Eqa. (3.12) and subsequently linearised .It is Noted that ∆V1D=∆v1Q=0. The state and output equation for the network model are finally obtained as

X.N = [AN] XN + [BN1] uN1+ [BN2] uN2 + [BN3] uN3B				     (3.31)

Where

Matrices  , , and  are given in Appendix

The SVS bus voltage and current, and voltage at the generator terminals constitute the output of the network model .The α-β axis component of the generator terminal voltage are given as

Equation () is transformed to D-Q axis frame of the refrence and subsequently linearised to get the network output equation as

YN1 = [CN1]XN+[DN1]uN1+[DN2]uN2 +[DN3]UN3

Or

The output equation in terms of the SVS bus voltage is given by

Or

Where,

,      ,

,    ,

3.4 Static VAR System Model

The linearized model of SVS control system is considered here for dynamic performance study. The voltage regulator is assumed to be proportional plus integral (PI) controller. The salient feature of this representation is the modeling of TCR transients. The delays associated with the SVS controller and measurement unit are also incorporated. The ,  axis current entering TCR from network are expressed as:

Ls di2αdt + Rsi2α = V2α								(3.32)

Lsdi2βdt + Rsi2β = V2β

Where Ls, Rs represent the inductance and resistance of TCR respectively. By applying kron’s transformation to equation (3.25)

ω0LSI2Q+LSI2D+RSI2D=V2D							(3.33)

Or           i2D = 1Ls V2D − RsLsi2D −ω0l2Q						(3.34)

Fig.3.6    SVS Control System with Auxiliary Feedback

Similarly

(3.35)

Equations (3.34) & (3.35) can be rewritten as

i2D = BV2D − ω0Qi2D − i2Q	 							(3.36)

i2Q = BV2Q −ω0Qi2Q + i2D   								(3.37)

When Q = quality factor = ω0LSR

And B = 1ω0Ls

Linearizing (3.36) and (3.37) gives

Δi2D = ω0B0ΔV2D + ω0ΔBV2D −ω0Q Δi2D−Δi2Q  					(3.38)

Δi2Q=ω0B0ΔV2Q+ω0ΔB0V2Q−ω0QΔi2Q+Δi2D					(3.39)

Equations (3.38) and (3 .39) can be written in matrix form

+ ω0B0 1001 ΔV2DΔv2Q + ω0 ΔV2ΔV2 ΔBΔi2DΔI2Q=ω0−1Q−11−1QΔi2DΔi2Q         (3.40)

Z1 = Vref – Z2 + VF 					   	                      (3.41)

Where Vref is the reference voltage perturbation and VF is the auxiliary controller out put

ΔV2−KDΔl2=Z2+TMZ.2								(3.42)

Where V2 and l2 are the incremental magnitudes of SVS bus voltage and TCR current

Z.2=1TM(ΔV2−KDΔl2)−1TMZ2							(3.43)

Also    –KP Z1 – K1 Z1= Z3+TS Z3							(3.44)

Substituting Equation (3.42) in Equation (3.44) gives

Z.3 = −KIT3Z1 + KPTS Z2 −1TsZ3 − KPTSΔVref − KpTs ΔVF 				(3.45)

The SVS bus voltage V2 is expressed in terms of it D, Q axis components as

V22 = V2D2 + V2Q2     									(3.46)

Linearizing equation (3.46)

ΔV2 = V2DoV20 ΔV2D + V2D0ΔV2aV20   							(3.47)

Similarly the magnitude of TCR currents is given by

i22 = i2D2 + i2Q2 										(3.48)

Linearizing Equation (3.48) given

Δi2 = i2D0i20 Δi2D + i2i20 Δi2Q								(3.49)

Substituting Equation (3.49) and (3.47) in Equation (3.36) gives

Z.2 = 1TM (KVDΔV2D + KVQΔV2Q) − KD(KiD Δi2D + KiQ Δi2Q) − 1TM Z2		(3.50)

Where

KVD = V2D0V20 KVQ = V2QoV20

And  KiD = l2D0l20 KiQ = i2Q0i20

The state and out put equation of the SVS model can for written as: -

Or XS. = [AS] XS+[BS1] US1+[BS2] US2+[BS3] US3					(3.51)

The out put equation of the SVS is constituted by the TCR current and in given by

Δi.2DΔi.2QZ.1Z.2Z.3ΔB.=−RSLS−ω0000ω0V2D0ω0−RSLS000ω0V2Q0000−100−KDKiDTM−KDKiQTM0−1TM0000−KITSKPTS−1TS000001TD−1TDMΔi2DΔi2QZ1Z2Z3ΔB

+ 1LS001LS00KvDTMKVQTM0000 ΔV2DΔV2Q + 0010−KPTS0 ΔVref + 0010−KPTS0 ΔVF

orX.S=ASXS+BS1US1+BS2US2+BS3US3					(3.52)

The output equation of the SVS is constituted by the TCR currents and is given by

or Ys = Cs Xs + Ds US1								(3.53)

Where XS = [i2D i2Q  Z1  Z2 Z3 B]t, uS1= [V2D V2Q]t

US2 = [Vref], [uS3] = [ VF ], YS = [i2D i2Q]t

- 3.5 Development of the System Model

The state and out put equations of the different constituent subsystems are combined resulting in the state equation of the overall system. The various subsystem models are so derived that inputs to any subsystem are directly obtained as out put of the other subsystem Fig (4.1) considering the network transients. These interconnections considered to be a detailed representation of the generator and are valid for detailed as well as simplified representation of the SVS.

The overall system model can be developed as follows

X.= [A] X + [B] Vref								(3.54)

Where X = [XR XM XE XN XS]t    B = [0 0 0 0 BS3 0]t

The system matrix [A] is given by

| AR | BR1CM | BR2CF | BR3CN2 | 0 |
| --- | --- | --- | --- | --- |
| BM1CR1 | AM+BM1DR1CM | 0 | BM2CN2 | 0 |
| BEDN2CR1 + BEDN3CR2 | BEDN2DR1CM + BEDN3DR2CM | AE + BEDN3DR3CE | BECN1+ BEDN1DSCN3+ BEDN3DR4CN2 | 0 |
| BN2CR1 + BN3CR2 | BN2DR1CM + BN3DR2CM | BN3DR3 | AN+BN1DSCN3 +BN3DR4CN2 | BN1CS |
| 0 | 0 | 0 | BS1CN3 | AS |

The   overall dimension of the system matrix is 29 for the system model having the network representation with single lumped parameter ∏ circuit on either side of SVS.

CHAPTER 4

- AUXILIARY control of SVS

4.1 Introduction

It has been established that a SVS with only voltage control may not adequately contribute to the system damping [27, 28]. Significant enhancement in damping is achieved when SVS reactive power is modulated in response to auxiliary control signals superimposed over its voltage control loop. Various auxiliary control signals have been reported in the literature for system damping enhancement. These include deviation on angular velocity (8, 29), bus frequency tie line reaction power, active power derivative of active power and machine internal frequency. Discontinuous control strategies involving switching of TSR/TCR in accordance with active power flow in weak tie lines has also been suggested [30] for improving system damping. In chapter 4 various auxiliary signals for their comparative performance are analyzed.

Fig. 4.1 Schematic diagram of interconnection of various subsystems

4.2 Auxiliary Controller DESIGN

It is assumed that the auxiliary controller is a first order transfer function G(S) as shown in figure 4.2 The effect of any general first order auxiliary controller can be implemented through G(S).

G(S)=ΔVFΔfs=KB1+ST11+ST2							(4.1)

The controller can be made equal to

G(S)=KBT1T2+KB1−T1/T21+ST2								(4.2)

From the block diagram of figure 3.7

Fig. 4.2 General First Order Auxiliary Controller

ZCUC=KB1−T1/T21+ST2							(4.3)

Or	ZC.=−1T2ZC+KBT21−T1T2UC				(4.4)

Or	XC.=AXC+BUC						(4.5)

The out put equation of an auxiliary controller is given by

ΔVf=KBT1T2UC+ZC								(4.6)

Where

XC=ZC,AC=−1T2,BC=KB21−T1T2YC=ΔVf,CC=1,DC=KBT1T2					(4.7)

Line Reactive power auxiliary controller

The transmission line reactive power entering SVS bus form the generator end is given by

(4.8)

Linearising equation 3.62 gives the deviation in line reactive power

(4.9)

This is expressed in Matrix notation as

(4.10)

Where

,

And

The suffix ‘0’ indicates the corresponding operating values.

4.3 System Model with Auxiliary controller

The state and output equations of the constituent subsystems are combined to get the overall system model as described in chapter 3. The state equations of overall system in given by

XT = [A] XT + [B] Vref

Where [A] is given as

| AR | BR1CM | BR2CF | BR3CN2 | 0 | 0 |
| --- | --- | --- | --- | --- | --- |
| BM1CR1 | AM+BM1DR1CM | 0 | BM2CN2 | 0 | 0 |
| BEDN2CR1 + BEDN3CR2 | BEDN2DR1CM + BEDN3DR2CM | AE + BEDN3DR3CE | BECN1+ BEDN1DSCN3+ BEDN3DR4CN2 | 0 | 0 |
| BN2CR1 + BN3CR2 | BN2DR1CM + BN3DR2CM | BN3DR3 CE | AN+BN1DSCN3 +BN3DR4CN2 | BN1CS | 0 |
| BS3DCFCR | BS3DCFCM | 0 | BS1CN3+ BS3DCFCN | AS+ BS3DCFCS | BS3CC |
| BCFCR | BCFCM | 0 | BCFCN | BCFCS | AC |

And  XT = [XR, XM XE XM XS XC]t , B = [0, 0  0  0 BS2  0]t    [Vref]

This form of system matrix is defined in chapter 3. The dimension of system matrix after incorporating the SVS auxiliary controller becomes 29 for ∏ circuit.

The Eigen values analysis carried out for the system model developed without inclusion of any auxiliary control signal are listed in table 5.1

CHAPTER 5

  - Case Study

The study system consists of two 555 MVA synchronous generators represented by an equivalent 1110 MVA machine, supplying power to an infinite by over a long transmission line 400Kv, and 600km. The mid point connected SVS is rated at 300 MVA leading to 200 MVA lagging.

The synchronous machine is represented by its detailed sixth order model with automatic voltage regulator as described in chapter 3. The data corresponding to generator AVR and SVS including all control system delays is given in Appendix A4.

The objective of this study is to evaluate the comparative effectiveness of various auxiliary signals of SVS for enhancing the dynamic performance of transmission line in order to determine the most effective auxiliary control signal.

  - Dynamic Performance

The Eigen values have been computed for the system with and without auxiliary controller incorporated in the SVS control system in co-ordination with induction machine damping using ∏ circuit model of AC network.

The following SVS auxiliary controllers have been used in respect of then ability to stabilize the unstable system modes.

- Line reactive power auxiliary controller

- Bus frequency auxiliary controller

- Voltage angle auxiliary controller

- Combined active power and bus frequency (CAPF) auxiliary controller.

- Derivative of reactive power auxiliary controller.

- Derivative of active power (DAP) auxiliary controller.

5.3 Eigen values with and without auxiliary controller

Table 4.1 Shows the Eigen values without any auxiliary controller at generator power Pg = 200, 500 and 800 MW. When an auxiliary controller is incorporated, four unusable torsional modes 5, 4, 1 and 0 are investigated in the system at PG = 800 MW. At Pg = 500 and 200 MW, there torsional modes 5, 4 and 3 are unstable/ Remaining modes corresponding to generator, network and SVS are stable. Damping of mode 0 is greatly improved with increase in generator power while the damping of mode 4 and 1 decreases with increase in generator power.

Table 5.1 Eigen values of the study system with and without auxiliary controller of 200MW (∏ circuit model)

|  | Without Auxiliary Controller | With Reactive power auxiliary Controller |
| --- | --- | --- |
| Generator | -0.3±4.4i -2.4 -26.6 -34.6 -0.8+0.8i | -0.5±4.4i -2.4 -29.4 -32.2 -0.8+0.8i |
| AVR | -0.8±0.8i -25.9±23.9i | -0.8±0.8i -26±23.7i |
| Net Work | -3.7±3530.0i -3.7±2901.7i -30.6±2558.3i -15±1930.0i -11.7±1415.0i -14.6±787.5i | -3.7±3530.0i -3.6±2901.6i -13.6±2558.3i -14.9±1929.8i -13.8±1416.3i -8.3±785.1i |
| SVS | -5.6±312.1i -57±85.2i -547.5±87.2 | -5.3±311.1i -548.4±87.1i -62.3±88.1i |

Table 5.2 Eigen values of the study system with and without auxiliary controller of 500MW (∏ circuit model)

|  | Without Auxiliary Controller | With Reactive power auxiliary Controller |
| --- | --- | --- |
| Generator | -.1±4.6i -33.2 -30.4 -2.8 | -0.4±4.7i -31.8±1.8i -8.3 -2.8 |
| AVR | -0.7±.9i -25.9±24.1 | -0.7±0.8i -26.2±23.8i |
| Net Work | -3.2±3508.0i -3.2±2879.7i -13.2±2482.2i -14.9±1853.9i -11.8±1037.4i -20.1±707.3i -23.6±313.7i | -3.2±3508.0i -3.2±2879.6i -13.2±2482.2i -15±1853.8i -14.2±1038.1i -23.4±313.8i |
| SVS | -6.8±312.7 -56.2±87.3i | -6.7±311.0i -65.4±85.8i 547.8±65.1i |

Table 5.3 Eigen values of the study system with and  without auxiliary controller of 800MW (∏ circuit model)

|  | Without Auxiliary Controller | With Reactive power auxiliary Controller |
| --- | --- | --- |
| Generator | -0.2±4.3i -2.9 -32.1±0.9i -0.9±1.0i -2.9 | -0.6±5.0i -27.6 -34.7 -9.6 -2.9 |
| AVR | -51.2±97.5i -26.0±24.2i | -61.6±98.2i -26.4±23.8i -0.8±1.0i |
| Net Work | -3.2±3507.9i -3.2±2879.6i -13.2±2481.8i -14.9±1853.5i -12.9±1003.4i | -3.2±3494.2i -3.2±2865.9i 13.2±2468.8 -14.9±1840.4i -15.5±1002.9i |
| SVS | -547.7±69.1i -5.6±313.1i | -545.9±65.0i -7.9±373.0i -4.8±309.8i |

# CHAPTER 6

# CONCLUSIONS

- 6.1 GENERAL

In this chapter, a detailed system model has been developed for torsional interaction studies. The network has been represented by lumped parameter ∏-circuit. The model of synchronous generator is taken so as utilize it in dynamic stability analysis and system simulation. The excitation system is IEEE type I. A detailed SVS model is developed and incorporated in the system model. The order of the system without SVS auxiliary controller is 33.

From the analysis it is evident that some of the mechanical modes are not stable and inclusion of auxiliary control signal becomes evident.

The imminent deregulation of electrical energy utilities is forcing them to look for different means and ways to optimize and control their power transmission networks. Advanced power electronic devices and Flexible AC Transmission Systems (FACTS) technologies [27, 31] are providing the required solutions. A SVS is one type of power electronic equipment emerging under the aegis of FACTS devices for such purposes [32, 33, 26]. The SVS typically negotiates reactive power in shunt at the point of common coupling thereby allowing automatic regulation of that bus voltage and influences the voltage profile of power system in the vicinity. The core of this Project is the investigation of various auxiliary signals for SVS to damp various torsional modes in power system to improve its performance. The application of SVS for damping of the torsional oscillations examined in the IEEE first benchmark system [34]. The results from the analytical and digital simulation studies reveal that a SVS with PI controller to regulate the bus voltage, along with various auxiliary signals derived locally and induction motor damping unit can suppress the unstable torsional mode oscillations.

In this Project report SVS control system has been examined for dynamic performance Enhancement of power systems. The most effective SVS auxiliary controller is determined by Eigen value analysis with Matlab software. The Eigen values (with Auxiliary and without Auxiliary controller) of Generator, SVS, AVR and Network are negative which indicates that the ∏ network circuit is in stable mode.

Chapter 7

Scope for future work

The following are some of the interesting problems which could be investigated further based upon the work reported in the present thesis:

- The present thesis has examined the effect various auxiliary signals incorporated is SVS control system for dynamic performance enhancement of power system. Other auxiliary signals can be developed and incorporated in the control schemes of other FACTS devices i.e. TCSC, SSSC and UPFC etc. for enhancement of dynamic  performance of the power system.

- Effect of coordinated applications of may FACTS controllers can investigated for dynamic and voltage stability enhancement and damping of power system oscillations of further work.

- ANN and fuzzy logic based adaptive controllers for SVS can be developed.

- Economic comparative study can be made for effective FACTS controllers for enhancement of power transfer capability enhancement  to find out the most economic FACT controller.

- In addition to the detail designs implementation of SVS controller in Indian Power system can be investigated in detail.

Refrences

[1].	Anderson P.M. and Fouad A. A. “Power system control and stability”, Iowa State University Press, U. S. A, 1977.

[2].	Anderson P.M., Aggrawal B.L. and Van Ness J. E. “Sub synchronous resonance in Power Systems”, IEEE Press, New York, 1990.

[3].	Atef Aly El-Emary, “Effect of static VAR compensator upon synchronizing Torque coefficient” Electric Machines and Power Systems 25:371-386, 1997.

[4].	A.R. Messina, O. Begovich M. “Analytical investigation of the use of static Var compensators to aid damping of inter area oscillations,“Electric Power System Research 21(1999) 199-210.

[5].	 A.R. Messina, E. Barocio, “Nonlinear analysis of inter area oscillations effect of SVC voltage support.” Electric Power System Research, Vol. 64, 1(2003) 17-26.

[6].	A.H.M.A. Rahim, M.F. Kandlawala, “Robust STATCOM voltage controller design using loop-shaping technique.” Electric Power System Research, Vol. 60, Jan. 2004, 61-74.

[7].	A.H.Othman and Angquist Lennort, “ Analytical modeling of TCSC for SSR studies, IEEE Transaction on Power system, 11(1), Feb. 1996, 1119-127.

[8].	A.M. Harb, M.S. Widyan, “Modern non linear theory as applied to SSR of the IEEE second bench mark model”, IEEE Bologna Power Tech. Conference June 23-26, Bolgana, Italy, 2003.

[9].	Abdel-Magid, Y.L.Abido MA “Robust coordinated design of excitation and TCSC based stabilizer using genetic algorithms” Electric Power System Research, Vol.69, 2004, 129-141.

[10].	B.T. Ooi and M.M. Sartawi," Concepts of field excitation control of sub synchronous resonance in synchronous machines, " IEEE Transactions on Power Apparatus and Systems, Vol. PAS-97, NO, 5, pp. 1637-1645, September/October 1978.

[11].	Belurs B.T., Ashok Kumar, K Parthasarthy et al “Effectiveness of series capacitor in long distance transmission lines” IEEE Transaction on Power Apparatus and System May 1970, pp. 941-950.

[12].	Djukanovic, M., Khammash, M. and Vittal, V. “Sequential synthesis of structured singular value based decentralized controllers in power systems”, IEEE Transaction on Power System, 1 999, 14, (2), pp. 635–641

[13].	Edris Abdel-Aty, “Sub synchronous resonance countermeasures using phase imbalance”, IEEE Transaction on Power Systems, Vol.8. No. 4, Nov. 1993, pp. 1438-1445.

[14].	E.W. Kimbark, “Improvement of system stability by switched series capacitors” IEEE Transaction on Power Apparatus and Systems Vol. PAS-85, No. 2, 1966,pp. 180-188.

[15].	Balasubramanyam P. V., Murthy A. S. R. and Parameswaran S., “Damping torsional oscillations – A Coordinated Approach”, Electric Machines and Power Systems, Vol.22, 1994, pp. 233-257.

[16].	Balda J.C., Eitelberg, E. and Harley R.G., “Optimal output feedback design of shunt reactor controllers for damping torsional oscillations”, Electric Power System Research, Vol.10 1986 pp. 25-33.

[17].	Bhatti T.S. and Kothari D. P. “Compensation of long distance transmission lines”, Proceedings. N.S.C.-90 A.M.U. Aligarh (India) pp. 63.

[18].	B.N.Singh, Bhim Singh, Ambrish Chandra, Kamal Al-Hadded “Digital implementation of an advance static compensator for voltage profile improvement, power factor correction and balancing of unbalanced reactive loads” Electric Power System Research 54,(2000) 101-111.

[19].	B. Vishwanathan “Effect of series compensation on voltage stability of EHV long lines”, Electric Power System Research J. 6(1983) 185-191.

[20].	Chen X.R., Pahalawatha N.C. Annakkage U.D. and Kumble C.S. “Enhancement of multimachine power system stability using controlled series compensation with local feedback control”, Proceedings of NPSC Dec. 14-17,1994, New Delhi, pp. 102-108.

[21].	C.R. Fuerte, Esquivel, E. Acha, H. Ambriz-Prez, ”A thytistor controlled series compensator model for the power flow solution of practical power networks” IEEE transaction on Power System Vol. 15 No.1 Feb. 2000.

[22].	Chang C.S. and Huang J.S. “Optimal SVS placement for voltage stability reinforcement”, Electric Power System Research, Vol. 42, pp.165-172.

[23].	Gyugyi L. and et al., "The unified power flow controller- A new approach to power transmission control," IEEE Transactions on Power Delivery, vol. 10, no. 2, pp. 1085-1097, April 1995.

[24].	Ian A. Hisken, Cameron, Mclean, B., “SVC behavior under voltage collapse conditions”, IEEE Transaction on Power System, Vol. PWRS 7, No.3, August, 1992, pp. 1078-1187.

[25].	M.E. Rahman, M. Ahmed, and et al, "UPFC application on the AEP system -planning considerations," IEEE Transactions on Power Systems, vol. 12, no. 4, pp. 1695-1701, November 1997.

[26].	Angquist L., Lundin B., Samuelsson J. “Power oscillations damping using controlled reactive power compensation: A comparison between series and shunt approaches”. IEEE Transaction on Power Systems, Vol. 8 No. 2 May 1993, pp. 687-699.

[27].	A. Yan and Y.N. Yu," Multi-mode stabilization of torsional oscillations using output feedback excitation control," IEEE Transactions on Power Apparatus and Systems, Vol. PAS-101, pp. 1245-1253, 1982

[28].	Gyugyi L., “Control of shunt compensation with reference to new design concepts”, IEE Proceedings, Vol. 128, pt. C No.6, pp. 374-381, Nov. 1981.

[29].	Ghosh A. and Ledwich Gerard, "Thyristor controlled reactors in flexible AC transmission systems Part-1: Series compensation, Part-2 Shunt compensation”, Proceedings of the Eighth National Power System Conference, Dec. 14-17, 1994, New Delhi, pp 184-192.

[30].	Laszlo Gyugyi, Colin D. Schauder, Kalyan K. Sen, “Static synchronous series compensator: A solid state approach to series compensation of transmission lines, IEEE Transactions on Power Delivery, Vol. 12, No.1, January 1997.

[31].	A.M. El-Serafi and A.A. Shaltout, "Control of sub synchronous resonance oscillations by multi-loop excitation controller," Paper A79 076-1, presented at the IEEE/PES 1979 Winter Meeting, New York, 1979.

[32]	Ali T. Al-Awami, Y.L.Abdel-Magid, M.A.Abido, “Simultaneous stabilization of power system using UPFC-based controllers”, Electric Power Components and Systems, 34:941-959, 2006.

[33].	Aboytes F., Arroyo G. and Villa G. “Application of static VAR compensators in longitudinal power systems”. IEEE Transaction on Power Apparatus and Systems, Vol. PAS – 102, pp. 3460-3466, Oct. 1983.

[34].	Cheng C.H. and Hsu Y.Y., “Damping of generator oscillations using an adaptive static VAR compensator.” IEEE Transaction on Power Systems, Vol. 17, No. 2, May 1992 pp 718-724.

[35].	Chilali, M., and Gahinet, P. “Multi-objective output feedback control via LMI optimization”, IEEE Transaction on Automatic Control, 1997, 42, (7), pp. 896–911

[36].	Demello F. P. “Exploratory concepts on control of series compensation in transmission systems to improve damping of multi machine system oscillations”. IEEE Transaction on Power Systems, Vol. 7, Feb, 1994, pp. 102-108.

[37].	D.Thukaram, Abraham Lomi, “Selection of static VAR compensator location and size for system voltage stability improvement”, Electric Power System Research 54(2000) pp. 139-150.

# Appendix A1

### Synchronous Machine Model

### Parameters

### The constants a1 – a8 are described as

a1a2a3a4=−ω0XfXh−Xfh2RfXh−RfXfh−RhXfhRhXf

a5a6a7a8=−ω0XgXk−Xgk2RgXk−RgXgkRkXgkRkXg

The constant b1 – b6 are given as

b1=ω0RfXdf,b2b3=−ω0XfXh−Xfh2RfXdfXh−XdhXfhRhXfXdh−XfhXdf

b4=ω0RgXqg,b5b6=ω0XgXk−Xgk2RfXqgXk−XqkXgkRkXgXqk−XgkXqg

The constant c1- c4 are given by

C1=XdfXh−XdhXfhXd} }  left (X rSub { size 8{f} } X rSub { size 8{h} }  rSup { size 8{'} }  - X rSub { size 8{ ital fh} }  rSup { size 8{2} }  right )} } ,C rSub { size 8{2} } = {  {X rSub { size 8{ ital dh} } X rSub { size 8{f} }  - X rSub { size 8{ ital fh} } X rSub { size 8{ ital df} } }  over  {X rSub { size 8{d} }  rSup { size 8{XfXh'−Xfh2

C3=XqfXk−XqkXgkXd} }  left (X rSub { size 8{g} } X rSub { size 8{k} }  - X rSub { size 8{ ital qk} }  rSup { size 8{2} }  right )} } ,C rSub { size 8{4} } = {  {X rSub { size 8{ ital qk} } X rSub { size 8{g} }  - X rSub { size 8{ ital gk} } X rSub { size 8{ ital qg} } }  over  {X rSub { size 8{d} }  rSup { size 8{XgXk−Xqk2

Where, xf, xh, xg, xk are reactance of the rotor coils specified by the subscripts.

Rf, Rh, Rg, Rk are resistances of the rotor coils specified by the subscripts.

xdf, xdh, xfh, xgk, xqg, xqk are mutual reactance’s between rotor coils specified by the subscripts.

The resistances and reactances of various rotor coils are defined as follows:

xdf = xdh = xfh = xd – x1, xqg = xqk = xgk = xq – x1

Xhl=Xd} }  - X rSub { size 8{1} }  right ) left (X rSub { size 8{d} }  rSup { size 8{'} }  - X rSub { size 8{1} }  right )}  over  { left (X rSub { size 8{d} }  rSup { size 8{'} }  - X rSub { size 8{d} }  rSup { size 8{,Xfl=Xd'−X1XdfXd−Xd'

Xgl=Xq} }  - X rSub { size 8{1} }  right ) left (X rSub { size 8{q} }  rSup { size 8{'} }  - X rSub { size 8{1} }  right )}  over  { left (X rSub { size 8{q} }  rSup { size 8{'} }  - X rSub { size 8{q} }  rSup { size 8{,Xkl=Xq'−X1XqkXq−Xq'

xf = xdf + xfl,  xh = xdf + xhl

xg = xqk + xgl,  xk = xqk + xkl

Rf=−Xdf2ω0Td0} }  left (X rSub { size 8{d} }  - X rSub { size 8{d} }  rSup { size 8{'} }  right )} } ,R rSub { size 8{h} } = -  {  { left (X rSub { size 8{d} }  rSup { size 8{'} }  - X rSub { size 8{1} }  right ) rSup { size 8{2} } }  over  {ω rSub { size 8{0} } T rSub { size 8{d0} }  rSup { size 8{

Rg=−Xq'−X12ω0Td0} }  left (X rSub { size 8{q} }  - X rSub { size 8{q} }  rSup { size 8{,Rk=−Xqk2ω0Td0} }  left (X rSub { size 8{q} }  - X rSub { size 8{q} }  rSup { size 8{'} }  right )} } } {

Where, x1 is the stator leakage reactance.

xd, xd', xd} } } { are the direct axis synchronous, transient and sub transient reactance, respectively.

xq, xq', xq} } } { are the quadrature axis synchronous, transient and sub transient reactance’s, respectively.

Tdo', Tdo} } } { are the direct axis transient and sub transient open circuit time constants, respectively.

Tqo', Tqo} } } { are the quadrature axis transient and sub transient open circuit time constants, respectively.

APPENDIX A-2

DERIVATION OF NETWORK OUTPUT

EQUATIONS

The network output equations used in Sec, 3.2.3.1, Chapter 3 are derived as given below:

The generator terminal voltage along  -  axis is given by

Vgα=Raiα+Ld} }  left ( {i}  cSup { size 8{ . } }  rSub { size 8{α} } +l rSub { size 8{α} }  right )}  {} # 
V rSub { size 8{gβ} } =R rSub { size 8{a} } i rSub { size 8{β} } +L rSub { size 8{d} }  rSup { size 8{i.β+lβ	          						(A (3.1)

Eqns. A (2.1) are transformed to D-Q axis frame of reference and subsequently linearized as

ΔVgD=RaΔid+Ld} }  left (Δi rSub { size 8{D} } +Δl rSub { size 8{D} }  right )+ω rSub { size 8{0} } L rSub { size 8{d} }  rSup { size 8{ΔiQ+ΔlQΔVgQ=RaΔiQ+Ld} }  left (Δi rSub { size 8{Q} } +Δl rSub { size 8{Q} }  right )+ω rSub { size 8{0} } L rSub { size 8{d} }  rSup { size 8{ΔiD+ΔlD				 A (3.2)

At node  2 in Fig. 3.6, we have

iα=−i2α+V2αjω0Cn+i1α  							 A (3.3)

ID+jiQ=−i2D+ji2Q+ji1Q+i1D+V2D+jV2Qjω0Cn

Comparing real and imaginary parts

iD =−(i20 + i1D − ω0cnv2Q)

iQ = −(i2Q + i1Q + ω0cnv2D 						 	 A (3.4)

Linearizing Eqns. A (2.4)

ΔiD = − (Δi2D +Δi1D − ω0cnv2Q)

ΔiQ = −(Δi2Q + Δi1Q + ω0cnv2D)  						A (3.5)

Substituting the ΔiD, ΔiQ and ΔiQ in A(2.2), the output equation in terms of generator terminal voltage can be obtained as given in (3.33).

APPENDIX A3

System Data

C.1 Data of Different System Components (143)  :

System Base Quantities

Voltage  = 400 KV

MVA = 100

Frequency = 50 Hz

Synchronous Generator Data (on its own base)

| Sn | = 1110 MVA |  | T’do | = 6.66 sec |
| --- | --- | --- | --- | --- |
| Vn | = 22 KV |  | T’qo | = 0.44 sec |
| pf | = 0.9 |  | T”do | = 0.032 sec |
| fn | = 50 Hz |  | T”qo | = 0.057 sec |
| Ra | = 0.0036 pu |  | Xd | = 1.933 pu |
| X1 | = 0.21 pu |  | Xq | = 1.743 pu |
| R0 | = 0 pu |  | X’q | = 0.467 pu |
| X0 | = 0.195 pu |  | X’q | = 1.144 pu |
| H | = 3.22 sec |  | X”d | = 0.312 pu |
| D | = 0 |  | X”q | = 0.312 pu |

This corresponds to a single generator mass

Data for sending and Receiving End Transformers (on generator base)

RT =  0.00 pu 	XT = 0.15 pu

IEEE Type I Excitation System Data

Vg = 1 pu 	TR = 0 sec

Vf = 1 pu 	KA = 400 pu

Vpss = 0	TA = 0.02 sec

Vrms = 9.75 pu	KE = 1.0 pu

Vrmin = -7 pu 	TE = 1.0 sec

Vfmax =  5 pu 	Kf = 0.06 pu

Vfmin = -7 pu 	TF  = 1.0 sec

SEmax = 0.95 	SEmin = 0

Transmission Line Data

| Voltage | 400 KW |
| --- | --- |
| No. of conductors | 2 |
| Area of conductors | 0.4 inch2 |
| Resistance (R) | 0.034  per phase per Km. |
| Reactance (XL) | 0.325  per phase per Km. |
| Susceptance (BC = 1/XC) | 3.68 x 10-6 mho per Km. |
| Charging current | 0.845 A per phase per km. |
| Surge impedance | 296  |
| Natural Load | 540 MW |
| XL / R ratio | 9.5 |
| Thermal Rating : |  |
| Cold weather (<400F) | 1100 MVA |
| Normal (400 – 650 F) | 900 MVA |
| Hot weather (<650F) | 790 MVA |

Static VAR System (SVS) Data

Configuration: Switched Capacitor – Thysistor Controlled Reactor (SC-TCR) to be switched in step of 1.0 p.u.

| Nature of operation | 6 pulse |
| --- | --- |
| Coupling of Transformer | Y/ |
| Q- Factor of TCR = 100 |  |
| TM = 2.4 msec | KI = 1200 |
| TS = 5 msec | KP = -1.0 |
| TD = 1.667 msec | KD = 0.01 p.u |

C. 2 Torsional System Data (on generator base)

| Mass | Shaft | Inertia H (Sec) | Spring Constant (Pu torque / rad) |
| --- | --- | --- | --- |
| HP |  | 0.1033586 |  |
|  | HP-IP |  | 25.772 |
| IP |  | 0.1731106 |  |
|  | IP-LPA |  | 46.635 |
| LPA |  | 0.9553691 |  |
|  | LPA-LPB |  | 69.478 |
| LPB |  | 0.9837909 |  |
|  | LBP-GEN |  | 94.605 |
| GEN |  | 0.9663006 |  |
|  | GEN-SEC |  | 3.768 |
| EXC |  | 0.380697 |  |

All self and mutual damping coefficients are assumed to be zero.

The various turbo generator masses are described as follows;

| HP | : | High Pressure Turbine |
| --- | --- | --- |
| IP | : | Intermediate Pressure Turbine |
| LPA | : | Low Pressure Turbine A |
| LPB | : | Low Pressure Turbine B |
| GEN | : | Generator |
| EXC | : | Exciter |