SIMULATION OF COGENERATION SYSTEMS

A Dissertation report submitted

By

YOGESH UPADHYAY

College Roll No: 07/THR/05

University Roll No: 2204

Under the Guidance of

Dr. S. S. Kachhawaha

And

Dr R. S. Mishra

In partial fulfillment of the requirements for the award of the degree of

Master of Engineering

In

Thermal Engineering

Department of Mechanical Engineering,

Delhi College of Engineering, University of Delhi

Session 2006-07

CERTIFICATE

This is to certify that the project report on “Simulation of Gas Turbine Cogeneration Systems” submitted by Yogesh Upadhyay for the partial fulfillment of the award of the degree of ‘Master of Engineering’ in Thermal Engineering. at Delhi College of Engineering is a record of bonafide work carried out by him under my guidance in the academic year 2006-2007.

The matter embodied in this project has not been submitted for the award of any other degree.

Dr.S.S.Kachhawaha

Assistant Professor

Department of Mechanical Engineering

Delhi College of Engineering

ACKNOWLEDGEMENTS

It is a great pleasure to have the opportunity to extent my heartiest felt gratitude to everybody who helped me throughout the course of this dissertation. It is distinct pleasure to express my deep sense of gratitude and indebtedness to my guide Asst. Prof. S.S. Kachhwaha and Asst. Prof.R.S.Mishra, Department of Mechanical Engineering, Delhi College of Engineering, for his invaluable guidance, encouragement, and patient review. His continuous inspiration only has made me complete this Minor project thesis.

I would also like to take this opportunity to present my sincere regards to my teachers for their kind support and encouragement.

I am thankful to my friends and classmates for their unconditional support and motivation for this seminar.

YOGESH UPADHYAY

Roll No.: 2204

Abstract

In the present times of fast depleting fuel resource growing concern for environment and ever-increasing demand for electricity, the need for a more efficient and less polluting power plant is occurring. In this respect, the Gas turbine cogeneration system is a suitable system to present an attractive concept. Mainly three types of cogeneration systems viz. simple gas turbine cogeneration system, Gas turbine cogeneration system with regeneration and Gas turbine cogeneration system with alternative regeneration has been used in past decade offering a significant increase in cycle efficiency along with other environmental advantages.

Gas turbine cogeneration systems are simple system with number of diverse components such as compressor, gas turbine, heat exchanger and combustion chamber, connected in interactive loop. In the present work attempt has been made to understand the performance of three above mentioned Gas turbine cogeneration systems based simulation by the characteristics equations of different components.

The first phase of work involves concerned literature review. From these studies, it is concluded that there is opportunities to execute analysis to compare the superiority of three systems.

In the second phase of work the Tables of for validations of properties of fluids with the paper value is done. For this table the calculated values differ from the book by 0.05%. The steady state simulation have been presented and developed to predict the performance of the gas turbine cogeneration systems from known performance characteristics of its main components.  In order the procedure could be validated, the simulation technique has been applied to typical systems of gas turbine cogeneration system viz. regeneration system and alternative regeneration system. It is observed that the reference values and calculated values for various important parameters are matching within 1%.

In the final phase of the work, graphical representation of different tables is given. First law efficiency, power output is shown varying with pressure ratio and turbine inlet temperature. The results indicated the superiority of Gas turbine cogeneration system with alternative regeneration in terms of First law efficiency etc. Furthermore, this system has economical and environmental advantages over other two systems.

CONTENT

Certificate                                                                                                            i

Acknowledgements									  ii

Abstract										           iii

Nomenclature									      vi-vii

List of Figures 									     viii-ix

List of tables										   x

# 1 Introduction

1.1 Simple gas turbine cogeneration system

1.2 Modeling and Simulation

# 2 Literature Review

2.1 Summary of Literature Review

2.2 Review of Simulation and Computer Modeling

2.3 Conclusions from Literature Review

# 3 Properties of working Fluid

3.1 Properties of Air

3.2 Properties of Fuel

3.3 Properties of Combustion Gases

4 Introduction and Formulation of gas Turbine Cogeneration System

4.1 Formulation of Simple gas Turbine Cogeneration System

4.2 Formulation of gas Turbine Cogeneration System with regeneration and with alternative regeneration

5 Modeling of the gas turbine cogeneration system

5.1 Introduction

5.1.1 Compressor

5.1.2 Combustion Chamber

5.1.3 Gas Turbine

5.1.4 Regenerator

5.1.5 Heat Recovery Steam Generator

# 6 Computer simulation of gas turbine cogeneration system

6.1 Simulation procedure

6.2 Steps in Simulation

6.2.1 Preparing Equation

6.2.2 Implementing Newton Rapsons Method

6.2.3 Jacobian Matrix

6.3 Results

# 7 Conclusions

# References

# Appendix A

Appendix B

Appendix C

NOMENCLATURE

a	  Air to fuel ratio

M	  Mass flow rate, (kg/s)

T	  Temperature of the fluid, (K)

P	  Pressure of the fluid, Bar

rp	  Compression Ratio

η	  Efficiency

cp	  Specific heat of the fluid, (kJ/kg)

H	  Enthalpy of the fluid, (kJ/kg)

h	  Specific enthalpy,(kJ/kg)

hf	  Enthalpy of formation,(kJ/kg)

I           Irreversibility, (kJ/kg)

Q	  Heat Transfer, (kW)

R	 Universal gas constant

S          Entropy, (kJ/kgK)

V	 Specific volume, (m3/kg)

W	  Work, (kW)

TIT	 Turbine Inlet temperature, (K)

SC       Simple cycle gas turbine

CGC    Conventional regenerative gas turbine

ARC    Alternative regenerative cycle

CHP    Combined heat and power

LHV    Lower heating value of fuel, (kJ/kg)

Greek letters

γ     Ratio of specific heats

εr    Effectiveness of the regenerator

Subscript

a	Air

f	Fuel

w        Water

g	Gas

t	Turbine

c	Compressor

Net	Net value

1        Compressor inlet

2        Compressor outlet

3        Regenerator inlet

4        Turbine inlet

5        Turbine outlet

6         Power turbine inlet

7         Power turbine outlet

exh      Exhaust

p         Product

R        Reactants

in       Incoming

hpt     High pressure turbine

pt       Power turbine

o        Reference value

List of Figures

Chapter1

Figure1.1 General Arrangement of cogeneration system

Chapter 4

Figure 4.1 Simple gas turbine cogeneration system

Figure 4.2 T-s diagram simple gas turbine cogeneration system

Figure 4.3 Gas turbine cogeneration system with regeneration

Figure 4.4 T-s diagram of Gas turbine cogeneration system with regeneration

Figure 4.5 Gas turbine cogeneration system with alternative regeneration

Figure 4.6 T-s diagram of Gas turbine cogeneration system with alternative regeneration

Chapter5

Figure 5.1 Input output parameters of Compressor

Figure 5.2 Input output model of regenerator

Figure 5.3 Input output model of the Combustor

Figure 5.4 Input output model of Turbine

Figure 5.6 Input output model of Heat recovery steam generator

Chater6

Figure 6.1 Flow chart of computer program for simple gas turbine cogeneration system

Figure 6.2 Flow chart of computer program for simple gas turbine cogeneration system with Regeneration

Figure 6.3 Graph between exergy destructions in each component of gas turbine cogeneration system

Figure 6.4 Graph between exergetic efficiency of gas turbine cogeneration systems

Figure 6.5 Variation in Second law efficiency of gas turbine cogeneration systems with      Pressure ratio

Figure 6.6 Variation of Irreversibility in Regenerator with Pressure Ratio in Gas Turbine Cogeneration systems

Figure 6.7 Variation of Irreversibility in exhaust gases in gas turbine cogeneration

Systems with Pressure ratio

Figure 6.8 Variation in Second law efficiency of gas turbine cogeneration systems with turbine inlet temperature

Figure 6.9 Variation of compressor exergy destruction with pressure ratio

Figure 6.10 Variation in Gas turbine exergy destruction with pressure ratio

Figure 6.11 Variation of Second law efficiency of each component with pressure ratio of gas turbine cogeneration system with alternative regeneration

Figure 6.12 Variation of Second law efficiency of each component with pressure ratio of gas turbine cogeneration system with alternative regeneration

Figure 6.13 Variation in First law efficiency with pressure ratio

Figure 6.14 Variation in First law efficiency with Turbine Inlet Temperature

Figure 6.15 Variation of Cycle Efficiency and Specific Workout put

INTRODUCTION

Cogeneration system may be defined as a thermal system that produces electric power and heat energy simultaneously from a single source of fuel. The use of electricity and process heat for various domestic and industrial applications is increasing rapidly. Consequently the demand for this type of energy is growing exponentially. On the other hand the fuel resources are diminishing, the fuel costs are also rising and there is a growing concern against environmental pollution by environmental norms. All these trends spell out the urgency of evolving highly efficient and economic models of power generation simultaneously a judicious and less polluting use of the limited reserves. While a long term strategy will necessitate shifting to more and more renewable resources.

In recent years, there have been substantial improvements in the performance of the gas turbines and gas turbine cycles are becoming more viable for power generation. Nevertheless, because of high exhaust gas temperature, waste heat from these plants is very high. During last two decades, attempts to use the gas turbine as a cogeneration system through a waste heat recovery boiler for effective utilization of resources have been implemented. These power plants give step-increase in efficiency and have reduced pollution effects with some other advantages in terms of process heats.

With ever growing demand of power for uninterrupted functioning, industries have started to concentrate on their own power plant. This power plant is mainly used for power requirement but have a significant roll in providing heat to the utilities of the industry. This heat is either available in the form of steam or hot water. Thus gas turbine cogeneration plant gains its undisputed importance in the industries.

The era around 1970 is known to be golden for developing gas turbine cogeneration plant. As in this duration the oil and gas has a prime and profitable market. Refineries need lots of process heat as well as power for its operation. Thus in refineries, cement plants and chemical industries the gas turbine cogeneration plant have been recommended frequently by their designer. The gas turbine cogeneration plant have been developed to a new horizon as the issues are now changing towards gaining more efficiency, reduction of fuel cost and protection of environment from the combustion gases.

Gas turbines cogeneration system are delivering the combined heat and power (CHP). CHP systems have applications both in large centralized power plants, and in distributed generation settings. Cogeneration systems have applications in centralized power plants, large industrial settings, large and medium sized commercial settings, and even smaller residential or commercial sites. The key determinant of whether or not combined heat and power technology would be of use is the nearby need or purpose for the captured waste heat. While electricity may be transferred reasonably efficiently across great distances, steam and hot water are not as transportable.

1.1 Simple gas turbine cogeneration system

Feed water

Saturated vapor

Regenerator

MA, T1, P1

Compressor

Turbine

Combustor

Power output

2

Figure 1.1 Simple gas turbine cogeneration system

HRSG

Combustion gases

8

3

4

9

Fuel

5

6

7

1

Figure 1.1 shows how the gas turbine system can be utilized as a cogeneration system that can produce both power as well as process heat. In this case, the gas turbine is generating power and by utilizing the exhaust gases low-pressure steam is produced for is wide use in refining, mining and other industrial application.

1.2 Modeling and Simulation

A mathematical model is an abstract model that uses mathematical language to describe the behavior of a system. Mathematical models are used particularly in engineering system design and analysis. A computer simulation or a computer model is a computer program that attempts to simulate an abstract model of a particular system. Computer simulations have become a useful part of mathematical modeling of many natural systems in engineering. A simulation is an imitation of some real thing, state of affairs, or process. The act of simulating something generally entails representing certain key characteristics or behaviors of a selected physical or abstract system.

Modeling a physical system by using experimental data in order to simulate the physical system is first step for simulation. Curve fitting techniques are used to derive mathematical equations to describe the performance of a system in terms of either its design variables or operating conditions. These equations are then programmed to run either on analogue or a digital computer in order to simulate the physical system. Although modeling by scaling down physical systems has been in use for a long time, computer modeling is relatively recent. However, it should be noted that the quality of simulation depends on the reliability of the experimental data that were used to develop the analytical model of the system. Computer models of engineering systems such as the aero and industrial gas turbine engines are developed mostly by mathematicians and computer software specialists who, quite often, may lack proper understanding of the physical characteristics of the systems they are trying to model. Such models are semi-empirical and are based on a limited amount of experimental data. The source of data quite often may not be traceable; for example, modeling the fuel system for a gas turbine engine from a single fuel delivery curve in order to develop the fuel control system.

In present study, after reviewing various aspects of the gas turbine cogeneration systems, an attempt is made to develop simple procedures of the performance prediction to understand wide range of performance characteristics of the gas turbine cogeneration system.

CHAPTER 2                                                                                    	                                                                                       LITERATURE REVIEW

The interest in gas turbine cogeneration system was aroused through out the world in early 1970s. During the last three decades a number of alternatives have been developed or added to the cogeneration system. In this chapter a detailed review of the literature on gas turbine cogeneration system has been undertaken, which evaluates various gas turbine cogeneration system arrangements consisting of simple gas turbine cycle couples to heat recovery steam generator. In addition, the methods of thermodynamic analysis and simulation of these systems available in the literature have been reviewed. Gas turbine cogeneration system is an extensive area of research, in which several researchers have already made some mark and several others are indulging themselves in this direction. A brief survey of Literature review is given below.

2.1 Summary of Literature Review

Hwang S.H., et al [1], have analyzed design and off design characteristics of the Alternative recuperative gas turbine cycle with divided turbine expansion, In this work they have performed both design and off design analysis. In this paper two types of designs are taken single and double shafts. The part load analysis has been carried out with the aid of realistic component maps and models for off design operations. In addition to the general fuel control, a variable speed control is assumed as the part load operating strategy of the single shaft configuration. Obvious advantage with the alternative cycle is observed in the variable speed operation of the single shaft design. With this strategy, the part load efficiency of the alternative cycle is far superior to the conventional cycle. Almost constant efficiency is predicted for a whole power range in their work.

Dellenback [2], have studied improved gas turbine efficiency through Alternative regeneration configuration. This paper considers the usefulness of cycle using the conventional regeneration. This revised modeling shows that the Alternative regenerative cycle can produce efficiency higher than conventional and simple cycle. This paper optimized the pressure ratio at all points for maximum possible efficiency. Turbine inlet temperature (TIT) is taken rather higher for current design value to examine the both current and future feasibility of cycle.

Korakianitis T., et al [3], have performed parametric analysis of combined cogeneration power plants with various power and efficiency enhancement. In this paper they have analyzed design-point performance characteristics of a wide variety of combined cogeneration power plants. They have prepared a computer program to evaluate the performance of the various power plants using standard inputs for components efficiencies, and the design point performance of these plants is computed. They have presented the result as thermal efficiency, specific powers, effectiveness and specific rate of energy in district heating. The performance of simple cycle gas turbine dominates the overall plant performance; the plant efficiency and power are mainly determined by turbine inlet temperature and compressor pressure ratio. They have also studied the performance under the condition varying steam injection and varying supplementary firing. Then a method of fuel cost allocation between electricity and hot water is recommended.

Dellenback [4], studied a reassessment of alternative regenerative cycle. This paper reconsidered the usefulness of cycle using the conventional regeneration. This revised modeling shows that the alternative regenerative cycle can produce efficiency higher than conventional only for limited set of conditions. This paper optimized the pressure ratio at all points for maximum possible efficiency. The turbine inlet temperature (TIT) is taken rather higher for current design value to examine the both current and future feasibility of cycle.

Stocker W.F. [5] has undertaken the problem of simulating a gas turbine power plant for the given characteristic curves of gas turbine and compressor. He has used these characteristics of compressor and gas turbine in the form of characteristics equations. In their work they have used seven variables with seven known equations, these equations includes the characteristics equations, mass balance equation and energy balance equations. To find the solution of the problem he has used Newton-Rapsons method for seven variables. He has shown that the solution is obtained within five iteration. The Newton Rapsons method converges very fast.

Seyedan B., et al, [6] have made a model to simulate and optimize the combined cycle power plant. In their study they have firstly analyzed various arrangements of gas turbine cycles. In addition to this computer based procedures have been developed to understand the performance of the combined cycle. After analyzing the performance of the system they have carried out the steady state simulation of to predict the performance of the combined cycle power plant from given performance characteristics of its main components. In final phase they developed procedure for optimum design of waste heat recovery boiler.

Kosman W., et al, [7], have simulated a thermal processes for performance control of CHP plant with a gas turbine unit. This paper presents a CHP plant with coal and gas fired sections. The power system consists of various units. The alteration of one of its units characteristics may significantly affects the operation of other units and of the whole system. Therefore, the performance control is very important task. The paper describes simulation modules of the flow processes as well as the suggested structure of the diagnostic investigation.

Li Y.G, et al [8], have performed an adaptation approach for the gas turbine design point simulation. In their work, they have proved that simulation and understanding of gas turbine performance is very useful for gas turbine users. They have analyzed simulated design point performance and actual measured performance, which were different. This difference may be reduced with better estimation of these unknown components parameters. In their work, a gas turbine design point performance adaptation approach has been developed to best estimate the unknown design point component parameters as compressor pressure ratio and efficiency, turbine entry temperature, turbine efficiency, mass flow rate of air, cooling flows, bypass ratio, etc.They have taken 29 MW gas turbine for the design point performance matching adaptation approach

Francisco S.B., et al, [9] have taken the cogeneration system simulation and control to      meet simultaneous power, heating and cooling demand. In their work the have simulated cogeneration system for control and storage demand dynamic model of a mid capacity system is developed, including gas and steam turbines with two heat recovery steam generators. They found that the power requirement could be generated exclusively with exhaust gases. The strategy in paper calls for fuel and steam flow rate modulation. The stability of the controlled systems and its performance are studied and simulation for different demand cases is performed

Moran [10], has established a design methodology for the Gas turbine cogeneration system. This simple system is integrated with Regenerator. A 30 MW Gas turbine is designed and air-fuel ratio is also calculated. Simultaneously the exergy and energy destruction at different points are also tabulated. From exhaust gases steam is formed at 20 bar and 14kg/sec, which is a assumption to design heat recovery steam generator.

Rio P.J., et al [12] has performed the thermo economic analysis of gas turbine cogeneration system. In their work they have carried out the energy and exergy analysis of 20 MW gas turbine cogeneration topping cycle plant with supplementary fuel firing to meet the process heat requirements at full and half load operating conditions. They have presented the energy and exergy diagrams. They have evaluated the plant performance on the basis of fuel utilization efficiency, power-heat ratio and second law efficiency. They have shown in their analysis that the exergy losses in combustion chamber and heat recovery steam generator are significant, Further pay back period at the full load conditions is also calculated.

Kumar and Krishna [14], has also shown the second law analysis of Gas turbine power plant with alternative regeneration. This work deals with thermodynamic analysis of a gas turbine alternative regeneration system and compares it with conventional regeneration configuration. The analysis deals with comparison of efficiency, work done and exergy loss. The results shows that, the alternative regeneration proved to be efficient than the conventional configuration.

Camporeale S., et al, [15] have created and analyzed a modular code for real time dynamic simulation of gas turbine in Mat lab- Simulink software. In their study a highly fidelity real time simulation code based on a lumped, nonlinear representation of gas turbine components is presented. The code is a general purpose simulation software environment useful for setting up and testing control of equipments. The mathematical model and the numerical procedure are specially developed in order to solve the set of algebraic and ordinary differential equation that describes the dynamic behavior of gas turbine system. They presented the model and the adopted solver procedure. They developed the code in Mat lab-Simulink using an object oriented approach, which is flexible and can be easily adapted to any kind of plant configuration. Simulation tests of the transient after load rejection have been carried out for a single shaft and double shaft gas turbine engines. Time plots of the main variables that describe the gas turbine dynamic behavior are shown and the results regarding the computation time per time step are also described.

Ramaprabhu V., et al, [16] have developed a computation model of a combined cycle power generation unit. In their study they predicted the performance of a local utility company combined cycle, by carrying out energy and exergy analysis of its components. The model is based on thermodynamic, heat transfer and psychometric principles, and includes an inlet air conditioning (fogging) system for a gas turbine cycle. In their work they compare the evaluated results and available plant tests at rated load with and without the inlet fogging system in operation.

Masumi iwai [24], have set the correlations of thermodynamic performance calculations of gas turbine engines. In his work he has taken one dimensional isentropic compressible flow function table, integrated with thermodynamic table to yield a subroutine program, which cab be utilized in the programming work relating with performance calculations in gas turbine. The table provides empirical relations of specific heat, enthalpy, entropy etc in terms of temperature for a wide range of temperature from zero to 5000K.

2.2 Review of Simulation and Computer Modeling

Steady state simulation is the technique of predicting the performance of the complex system at any operating point by using basic information about the system components, ambient conditions etc. In large systems involving heavy investments, where actual prototype building is not feasible, simulation provides a very potent tool for design. It is very handy in evaluating alternative concepts, alternative designs for components and part load performance characteristics at early design stage. Also it serves as pre requisite step for developing dynamic simulation for understanding the transient behavior as well as for taking up optimization studies. In context to any complex system, there are three types of simulation which serves complementary purpose, viz process or components simulation, steady state system simulation, dynamic system simulation. As the name suggests, process/components simulation involves detailed mathematical modeling of processes occurring in any components such as flow in a turbine etc. The purpose of such modeling is to gain more insight into the physical process and/or to mathematically generate component performance.

The system simulation requires as prerequisite performance characteristics of individual components either obtained from above modeling or correlations developed from manufactures data or empirically. Using the components characteristics developed in suitable form system compatibility equation are set up and solved simultaneously to yield overall system performance. The general procedure used for power plants steady state simulation has to be followed for simplified solutions. This includes defining a system; examine the system with the help of block diagrams, generating equations for each component characteristics, imposing the compatibility restrictions on the system carry out the simulation for various conditions using proper techniques.

Gay [25], developed a computer program written in Fortran for gas turbine evaluation, which perform detail design point analysis and steady state simulation over a wide range of a gas turbine power system combined cycle plant. This program also includes the thermodynamic analysis of heat recovery steam generator of a combined cycle plant.

Prez [26], developed a computer based method for thermodynamic power cycle calculation of conventional and advanced power plant. The program simulates various cycles by selecting components and connecting them in appropriate way.

2.3 Conclusions from Literature review

The researchers in the field of Gas turbine cogeneration system have already delivered a vast variety of work. However, the possibility of improving the domain of work is still there by combining different methods and methodologies of enhancing the performance of system. The main conclusions from the Literature review are pointed below.

Simulation and dynamic modeling of the gas turbine cogeneration system has been done in previous works. Design and analysis of cogeneration system along with the effect of regeneration on performance has also been done by some researchers. In addition to these work first law and second law analysis of gas turbine system with alternative regeneration is done, however the simulation studies of alternative regeneration is still untouched.

Thus there is an opportunity to implement simulation studies on gas turbine cogeneration system with alternative regeneration. It’s a further advantageous to compare the three systems of cogeneration viz simple cogeneration system, cogeneration system with regeneration and cogeneration system with alternative regeneration.

In present work the simulation of all the three cogeneration systems has been done and then after the three systems is compared. In this way the superiority of any of the three systems with respect to other two systems can be made. This serves as a reference for use of any particular system at any particular condition.

CHAPTER 3

PROPERTIES OF WORKING FLUIDS

The working fluids in cogeneration plants are air, fuel (Natural gas), water and steam. The correlation used to describe the properties of working fluids are given below.

3.1 Properties of air

The following relation [24] gives the variation of the specific heat with the temperature.

(3.1)

Air composition is taken, as it is present in the atmosphere. i.e.  79 % nitrogen, 21 % oxygen, 0.03 % carbon dioxide and 1.9% of water vapor [24].

Enthalpy and Entropy of air can be given as a function of temperature by following correlations.

(3.2)

(3.3)

where Co, C1, C2, C3, C4, CF and CH are thermodynamic coefficients. The values of Co, C1, C2, C3, C4, CF and CH are taken from table given in reference [24] and are given in Appendix A. In addition, the ratio of specific heat γ varies. This value is different for the diatomic gases, monatomic gases and polyatomic gases.

4.2 Properties of Fuel

Fuel taken in the present simulation is Natural Gas. This is mainly comprised of methane, ethane, propane, butane and carbon dioxide. Thus, all the properties like the enthalpy of formation, lower heating value and combustion reaction are taken for methane, ethane, propane, butane and carbon dioxide [6]. The composition of natural gas is taken as 84.71 % methane, 7.7 % ethane, 2.45 % propane, 1.3 % butane and 0.52 % carbon dioxide. Lower heating value of the natural gas for the above composition is taken from [10]. Heat of formation at reference condition is -74872kJ/kmol [10]. Other properties like heat of formation of different gases are tabulated in Appendix B.

4.3 Properties of Combustion gases

Combustion gases consist of gases like carbon dioxide, nitrogen, water vapors amd carbon monoxide. Thus, its specific heats and other properties depend on all its components. The specific heat value of a mixture of combustion gases is given as follows

=           	                                        (3.4)

where mi is the mass of the constituent of mixture

Cpi is the corresponding specific heat at constant pressure of constituent of mixture

(3.5)

where Cpa is the specific heat at constant pressure for air

Cpg is the specific heat at constant pressure for combustion gas

f is fuel-air ratio

θcp is correction factor for specific heat at constant pressure of combustion gases

The values of enthalpy and entropy for the combustion products can be given as follows, [24]

(3.6)

(3.7)

where ha is the enthalpy of air

θh is correction factor for enthalpy at constant pressure of combustion gases

θs is correction factor for entropy at constant pressure of combustion gases

The values of and  are given as follows

(3.8)

(3.9)

(3.10)

Where T is temperature, K

CPo,CP1,CP2,CP3,CP4,CP5, Ho,H1,H2,H3,H4,H5, Fo,F1,F2,F3,F4,F5 are thermodynamic coefficients given in Appendix A.. The above expression is derived from equation (3.4) on molar bases of different components in combustion gases. The value of gas constant for the combustion gases can be given as similar to the equation (3.4).

The polynomial coefficients for generating above equations are given in Appendix A.

CHAPTER 4

FORMULATION AND MODELING OF

GAS TURBINE COGENERATION SYSTEMS

The present chapter deals with formulation of the three systems of gas turbine cogeneration system. These three systems include simple gas turbine cogeneration system, gas turbine cogeneration system with regeneration and gas turbine cogeneration system with alternative regeneration.

4.1 Simple gas Turbine cogeneration System

Simple gas turbine system includes compressor, combustion chamber, gas turbine and heat recovery steam generator. The schematic of this system is in Figure 4.1.

MA, T1, P1

Compressor

Turbine

Combustor

Power output

2

Figure 4.1 Simple gas turbine cogeneration system

Fuel

1

3

4

HRSG

Steam

7

Exhaust 5

6 water

Figure 4.1 represents the simple gas turbine cogeneration system with air enters in compressor followed by combustion chamber where fuel is inducted and finally combustion product expand in the turbine to generate power output. The cycle of operation is shown in Figure 4.2.

1

2

2s

3

4

4s

T

S

PDC

1-2 Compression

2-3 Combustion

3-4 Expansion

4-5 HRSG

PDC pressure drop in combustor

5

Figure 4.2 T-s diagram for simple gas turbine cogeneration system

In combustion chamber the temperature can be calculated by balancing the heat of formation of all reactants and products. This is called adiabatic mean flame temperature. Combustor also causes the reduction in pressure of gas stream. The enthalpy balance in the combustor between reactants and products is given below. There is a slight drop in pressure at combustor. In Figure 4.2 process 4-5 shows the heat recovery steam generator.

4.2 Gas Turbine Cogeneration System with regeneration and with alternative regeneration

Regeneration in gas turbine is widely used to save the fuel in the combustion chamber. The high temperature exhaust gases from the turbine are used to preheat the compressed air before the combustion chamber. The schematic of the system is given as follows in Figure 4.3

Feed water

Saturated vapor

Regenerator

MA, T1, P1

Compressor

Turbine

Combustor

Power output

2

Figure 1.1 Simple gas turbine cogeneration system

HRSG

Combustion gases

8

3

4

9

Fuel

5

6

7

1

Various processes of gas turbine cogeneration system with regeneration are represented by T-s diagram in Figure 4.4.

1

2

2s

8

3

4

4s

T

PDR

PDC

1-2 Compression

2-8 Regeneration

8-3 Combustion

3-4 Expansion

4-9 Heat transfer in       regenerator

PDR pressure drop in regenerator

PDC pressure drop in combustor

S

5

Figure 4.4  T-s diagram of gas turbine cogeneration system with regeneration

Gas turbine cogeneration system with alternative regeneration is an advance system in which the position of regenerator is changed. The schematic of the system is as shown in Figure 4.4.The system is having a high-pressure turbine and power turbine. The purpose of high-pressure turbine is to produce the power to drive the compressor. The power turbine is meant for producing the net power. In this system air after compression enters regenerator where it is heated by exhaust gases coming out of high pressure turbine, and thus the gases are expanded in the power turbine. The cycle of operation is given in Figure 4.5 and the T-s diagram in Figure 4.6.

Compressor

1

2

Regenerator

cc

High pressure

Turbine

Power turbine

HRSG

Exhaust

Water

Steam

8

3

4

9

5

Figure 4.5 Gas turbine cogeneration system with alternative regeneration

Fuel

MA

T1 P1

7

10

6

1

2

2s

8

3

4

9

10

10s’

T

S

1-2 Compression

2-8 Regeneration

8-3 Combustion

3-4 High Pressure       turbines

4-9 Regeneration

9-10 Power turbine

10-5 HRSG

4s

5

Figure 4.6 T-s diagram for Gas turbine cogeneration system with alternative regeneration

4.3 Modeling of gas Turbine Cogeneration System

Modeling is a very convenient method of testing the behavior of large engineering systems of various levels of complexity. A convenient method to overcome this difficulty is to model the complete system by using the actual performance characteristics of the compressor and the turbine to prepare lookup tables. The main components of a Gas turbine cogeneration system are compressor, regenerator, combustor, gas turbine and heat recovery steam generator. Testing of either the components or the complete gas turbine engine for the purpose of obtaining performance characteristics can be a laborious and expensive exercise. Two types of modeling techniques are widely used; these are:

a. Modeling one physical system by another physical system that is designed to satisfy   certain similarity criteria. The later is a scaled down replica of the former. The science and the art of scaling and testing of models are well developed, therefore the test data can be corrected for effects of scale, blockage, end wall boundary layer etc.

b. Modeling a physical system by using experimental data in order to simulate the physical system. Curve fitting techniques are used to derive mathematical equations to describe the performance of a system in terms of either its design variables or operating conditions.

For the present study the models of different systems are developed by taking the characteristic equation of components. This is given in subsequent subsections.

4.3.1 Compressor

The characteristics of a gas turbine compressor are usually in the form of graphical relationship between three dimensionless numbers, namely compressor mass parameters (CMP), compressor pressure ratio (CPR) and the compressor efficiency (c) Fig 4.7 (a & b).These characteristics are most conveniently employed, if the mass flow rate to be handled by the compressor and the air inlet temperature and pressure are specified, as indicated in the information flow diagram Fig. 4.8, This input information enables computation of CMP, and using the characteristics curves (or the equation representing these), the compressor pressure ratio and the efficiency can be found. These can be   used to compute the work input to the compressor, the compressor discharge pressure (P2) and temperature (T2), by using basic thermodynamic relationships.

CPR=f1MT1P1,NcT1                                                                                             (4.1)

ηc=f2MT1P1,NcT1                                                                                                 (4.2)

CMP

CMP

CPR

ηc

(a)                                                                   (b)

Figure 4.7 Axial Compressor Characteristics

The equation form of these two characteristics curves are given below in Equation (4.3) and (4.4).

(4.3)

CPR=1.140CMP−0.1390                                                                             (4.4)

ηC=0.6712+0.22Pr                                                                                      (4.5)

where MA is the mass flow rate to the compressor (kg/s)

ηc is the efficiency of the compressor

CPR and CMP are dimensionless numbers and are to be calculated from characteristic equations.To1, Po1 are stagnation values of temperature and pressure and are given as follows

,                                                                                 (4.6)

where V1 is the velocity of air at compressor inlet and is calculated by V1=.The similar equations are applicable to turbine calculations. Pr is the pressure ratio and is given as the ratio of compressor outlet to compressor inlet pressure to compressor inlet pressure.                                                                                                                                  Pr=P2P1                                                                                                                          (4.7)

where P2 is the compressor outlet pressure kPa, P1 is compressor inlet pressure kPa.

T1 is the temperature of air at compressor inlet K

CMP is compressor mass parameters, CPR is compressor pressure ratio

These characteristics are most conveniently employed, if the mass flow rate to be handled by the compressor and the air inlet pressure and temperature are specified, as indicated in information flow diagram in Figure (4.8).

T2,   P2

Wc

TPR

ηc

TMP

MA

T1

P1

Figure 4.8 Information flow diagram for Compressor

Input information enables computation of CMP by using Equation (4.3). The Compressor Pressure ratio (CPR) and efficiency can be found by using Equation (4.5) and (4.7).

These can be used, to compute the work input to the compressor, the compressor discharge pressure (P2) and compressor discharge temperature (T2), by using following thermodynamic relationship.

(4.8)

Wc=CMPCpaT1P1(CPRγ−1γ−1)                                                                  (4.9)

where γ is the ratio of specific heat at constant pressure and constant volume

ΔT21 is the difference in compressor outlet and compressor inlet temperature K

Wc is compressor work consumed kW

4.3.2 Combustion Chamber

For the present study the fuel taken is natural gas composed of following constituents: Methane, Ethane, Propane, Butane, Carbon dioxide, Nitrogen, their respective percentage are 0.8451, 0.077, 0.0245, 0.0013, 0.052, 0.0001. Theoretical Air-fuel ratio is found to be 2.1, by the stochiometric equation [6]. Thus the combustion equation of reaction is

0.8451CH4 + 0.077C2H6 + 0.0245C3H8 + 0.0013C4H10 + 0.052CO2 + 0.0001N2 +   (2.1O2+2.1x3.76N2) 1.1298CO2 + 2.025H2O + (2.1x3.76 + 0.0001) N2

Thus the percent of theoretical air supplied is calculated as

(4.10)

The chemical reaction for complete combustion of natural gas with λ percent of theoretical air is written as,

0.8451CH4+0.077C2H6+0.0245C3H8+0.0013C4H10+0.052CO2+0.0001N2+(λ100×2.1)O2+(λ100×2.1×3.76)→1.1298CO2+2.025H2O+[(λ100−1)×2.1O2]+[λ100×2.1×3.76+0.0001]N2 According to the first law of steady state flow, adiabatic combustion process, the enthalpy of products and the reactants is equal, thus,

Σni(hfo+Δh)i=Σne(hfo+Δh)e                                                           (4.11)

Combustor Pressure drop is taken as PDC. Thus the pressure at combustor outlet is given as following equation

(4.12)

Adiabatic mean flame temperature is calculated iteratively so that Equation (4.11) is satisfied. The pressure drop in combustion chamber is taken as 2.5% of compressor outlet pressure. The information flow diagram of combustor is given in Figure 4.9

T2

MF

TIT (T3)

Combustor

MA

P3

P2

T2

Figure 4.9 Model of combustor

4.3.3 Gas Turbine

The characteristics of Turbine are also given by three dimensionless numbers, namely the turbine mass parameters (TMP), Turbine pressure ratio (TPR) and its efficiency (ηt) as shown in Figure 4.10.

TPR

TMP

TPR

ηt

(a)                                                                           (b)

Figure 4.10 Turbine Characteristics

The simulation of a turbine implies determination of TMP, ηt, turbine outlet temperature (T4) and the power output, for specified value of TPR and turbine inlet temperature (T3). The basic thermodynamic equation used in the turbine calculations are

(4.13)

From characteristic curve (4.10a)

Or          TMP=52.33+42.82TPR472.37                                                                             (4.14)

where TMP is dimensionless turbine mass parameter

TPR is the dimensionless turbine pressure ratio

(4.15)

From characteristic curve (4.10b)

ηT=0.9332−0.00250TPR						              (4.16)

For calculation of turbine outlet temperature

(4.17)

where ηt is the turbine isentropic efficiency

T3 is the temperature at turbine inlet K

Wt is the power output from the turbine kW

Work output of Turbine is given as

(4.18)

CHAPTER 5

Modeling of the gas turbine cogeneration system

HRSG

Gas Turbine

Combustor

Compressor

Energy balance

Saturated Steam T7, P7

Water T6, Patm

T5

P2

T2

ηc

CPR

CMP

TIT            T3

P3

PDR

TMP

ηt

MT

T4

T4

Figure 6.1 Information flow diagram for Simple gas turbine cogeneration system

T1

P1

MA

Wnet

Wc

Wt

HRSG

Regenerator

Gas Turbine

Combustor

Compressor

Energy balance

Saturated Steam T7, P7

Water T6, Patm

T5

P2

T2

ηc

CPR

CMP

T8

TIT T3

P4

PDR

TMP

ηt

MT

T4

T9

Figure 6.2 Information flow diagram for gas turbine cogeneration system with regeneration

T1

P1

MA

Wc

Wt

Wnet

Table 6.1 Newton-Rapsons solution of gas turbine cogeneration system simulation

[Fuel flow rate=6.23 kg/s, T1= 300K, Mf = 6.23 kg/s, P1=100.302 kpa, T5 = 485.5K, T6 = 298.150K, T7 = 625.50K, P9=20bar]

|  | Mass flow rate of air (kg/s) | Compressor outlet temperatureT2 (K) | Compressor discharge pressure P2 (kPa) | Compressor work Wc (kW) | Turbine inlet temperature T3(K) | Turbine outlet temperature T4(K) | Turbine power output Et(kW) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Trial values | 250.00 | 450.00 | 600.00 | 50000 | 900 | 700.00 | 120000 |
| Iteration 1 | 332.80 | 588.14 | 710.00 | 92000 | 1189 | 772.24 | 161000 |
| Iteration 2 | 345.81 | 596.24 | 725.01 | 95200 | 1201 | 788.21 | 164000 |
| Iteration 3 | 347.58 | 597.12 | 730.87 | 96310 | 1207 | 790.10 | 165320 |
| Iteration 4 | 347.58 | 597.12 | 730.87 | 96310 | 1207 | 790.10 | 165320 |

Table 6.2 Data table of various operating conditions at different air fuel ratio with rated values

| Fuel Flow Rate (kg/s) | Compressor inlet temperature T1 (K) | Compressor Air flow rate (kg/s) |  |  | Compressor Pressure ratio |  |  | Turbine inlet Temperature (K) |  |  | Power Output (kW) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Rated | Ref [6] | Computed | Rated | Ref [6] | Computed | Rated | Ref [6] | Computed | Rated | Ref [6] | Computed |
| 6.23 | 300 | 348.02 | 348 | 347.21 | 7.34 | 7.37 | 7.32 | 1214 | 12116 | 1213.02 | 69620 | 69530 | 69250 |
| 7.76 | 300 | 394.74 | 401.3 | 398.15 | 8.59 | 8.73 | 8.68 | 1276 | 1273 | 1272.34 | 99600 | 99900 | 99390 |
| 9.01 | 323 | 414.76 | 412.8 | 439.89 | 9.41 | 9.42 | 9.42 | 1377 | 1374 | 1373.25 | 117800 | 118450 | 117350 |
| 9.43 | 300 | 462.16 | 458.7 | 458.06 | 10.24 | 10.19 | 10.21 | 1328 | 1328 | 1327.09 | 130200 | 129950 | 129890 |
| 10.0 | 300 | 462.16 | 478.20 | 478.38 | 10.39 | 10.68 | 10.57 | 1363 | 1353 | 1352.29 | 139500 | 140500 | 139080 |

Table 6.3 Comparison of percentage error in various computed operating conditions between present work and rated values

| Fuel Flow Rate (kg/s) | Compressor Air flow (%) |  | Compressor Pressure Ratio (%) |  | Turbine inlet Temperature (%) |  | Power Output (%) |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Computed | Reference [6] | Computed | Reference [6] | Computed | Reference [6] | Computed | Reference [6] |
| 6.23 | 0.21 | 0.075 | 0.27 | 0.41 | 0.32 | 0.21 | 0.53 | 0.13 |
| 7.76 | 1.27 | 1.50 | 1.50 | 1.60 | 0.89 | 0.86 | -0.21 | -0.30 |
| 9.01 | 0.69 | 0.58 | 0.11 | 0.11 | -1.31 | -1.28 | -0.38 | -0.55 |
| 9.43 | 0.89 | 0.78 | 0.29 | 0.49 | -0.50 | -0.48 | 0.24 | 0.19 |
| 10 | 3.32 | 3.4 | 1.78 | 2.79 | 0.93 | 0.92 | -0.30 | -0.72 |

|  | MA (kg/s) | T2(K) | P2(kPa) | T3(K) | T4(K) | Ec(kW) | T8(K) | T9(K) | Et(kW) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Trial value | 250.00 | 450.00 | 600.00 | 900 | 700.00 | 50000 | 620.00 | 500.00 | 120000 |
| Iteration 1 | 308.25 | 534.21 | 672.24 | 1092 | 749.23 | 83210 | 701.23 | 582.34 | 178000 |
| Iteration 2 | 331.25 | 562.25 | 708.20 | 1180 | 771.08 | 95410 | 738.53 | 618.35 | 190210 |
| Iteration 3 | 348.29 | 589.29 | 727.20 | 1248 | 799.25 | 101250 | 772.25 | 641.54 | 201230 |
| Iteration 4 | 351.27 | 598.22 | 732.91 | 1287 | 802.98 | 105210 | 781.58 | 643.46 | 206510 |
| Iteration 5 | 351.27 | 589.22 | 732.91 | 1287 | 802.98 | 102210 | 781.58 | 643.46 | 206510 |

|  | MA(kg/s) | T2(K) | P2(kPa) | T3(K) | T4(K) | Ec(kW) | T8(K) | T9(K) | T10(K) | P9(kPa) | Et(kW) | Ept(kW) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Trial value | 250.00 | 450.00 | 500.00 | 900.00 | 750.00 | 50000 | 800.00 | 600.00 | 400.00 | 200.00 | 120000 | 70000 |
| Iteration1 | 323.23 | 498.97 | 681.53 | 1178.3 | 993.78 | 71210 | 897.51 | 688.81 | 450.51 | 246.68 | 97290 | 85600 |
| Iteration | 348.327 | 517.20 | 711.58 | 1250.1 | 1034.80 | 77670 | 927.80 | 707.35 | 469.38 | 258.81 | 92810 | 94812 |
| Iteration | 359.56 | 526.79 | 724.29 | 1282.5 | 1082.34 | 81581 | 942.71 | 713.28 | 479.97 | 263.05 | 86780 | 97871 |
| Iteration | 364.29 | 529.43 | 729.90 | 1297.7 | 1103.79 | 83982 | 951.12 | 717.89 | 486.35 | 264.77 | 85120 | 99820 |
| Iteration | 365.82 | 530.37 | 731.77 | 1299.8 | 1111.34 | 84053 | 955.30 | 720.35 | 488.39 | 265.98 | 84980 | 101.16 |
| Iteration | 366.67 | 531.05 | 733.20 | 1302 | 1114.59 | 84610 | 958.57 | 721.58 | 489.02 | 266.81 | 84610 | 102.98 |
| Iteration | 366.67 | 531.05 | 733.20 | 1302 | 1114.59 | 84610 | 958.57 | 721.58 | 489.02 | 266.81 | 94610 | 102.98 |

Table 6.4 Newton-Rapsons solution of simulation of gas turbine cogeneration system with regeneration                 [For mass flow rate of fuel 6.23 kg/s]

Table 6.5 Data table of various computed operating conditions at different air fuel ratio with reference values for gas turbine cogeneration system with regeneration

| Fuel Flow Rate (kg/s) | Compressor inlet Temperature T1 (K) | Compressor Air flow (kg/s) | Compressor Pressure ratio | Turbine inlet Temperature K | Power Output (kW) |
| --- | --- | --- | --- | --- | --- |
| 6.23 | 300 | 351.27 | 7.33 | 1287 | 101261 |
| 7.76 | 300 | 404.58 | 8.12 | 1336 | 129547 |
| 9.01 | 323 | 416.82 | 9.58 | 1359 | 162750 |
| 9.43 | 300 | 464.83 | 10.02 | 1376 | 192596 |
| 10.0 | 300 | 483.55 | 10.59 | 1409 | 212543 |

Table 6.6 Newton-Rapsons solution of simulation for gas turbine cogeneration system with alternative regeneration

[For mass flow rate of fuel 6.23 kg/s]

Table 6.7 Data table of various computed operating conditions at different fuel flow rate with reference values for gas turbine   cogeneration system with alternative regeneration

| Fuel Flow Rate kg/s | Compressor inlet Temperature T1 (K) | Compressor Air flow Kg/s | Compressor Pressure ratio | Turbine inlet Temperature K | Power Output (kW) |
| --- | --- | --- | --- | --- | --- |
| 6.23 | 300 | 366.87 | 7.34 | 1302 | 102587 |
| 7.76 | 300 | 408.73 | 8.22 | 1397 | 131592 |
| 9.01 | 323 | 421.02 | 9.53 | 1426 | 165831 |
| 9.43 | 300 | 463.82 | 10.09 | 1458 | 194790 |
| 10.0 | 300 | 488.71 | 10.63 | 1487 | 216356 |

Table 6.8 Comparison of three gas turbine cogeneration system based on same input condition (mass flow rate of fuel =6.23 kg/s)

Input conditions are T1= 300 K, Mf = 6.23 kg/s, P1=100.302 kPa, T5 = 485.5 K, T6 = 298.150K, T7 = 625.50K, P9=20 Bar

| Fuel flow rate(kg/s) | Power output (MW) |  |  | Specific Power Output (kJ/kg) |  |  | Saturated Steam Flow rate (kg/s) [at 20 Bar] |  |  | Cycle Efficiency (%) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | SC | CRC | ARC | SC | CRC | ARC | SC | CRC | ARC | SC | CRC | ARC |
| 6.23 | 69.25 | 101.26 | 102.58 | 187.4 | 282.2 | 284.4 | 41.50 | 18.74 | 9.45 | 22.25 | 32.52 | 33.10 |
| 7.76 | 99.39 | 129.54 | 131.59 | 244.4 | 314.4 | 316.6 | 45.78 | 20.25 | 10.52 | 26.13 | 33.84 | 34.22 |
| 9.01 | 117.35 | 162.75 | 165.83 | 278.2 | 381.1 | 385.7 | 51.68 | 22.65 | 12.54 | 26.72 | 36.03 | 36.80 |
| 9.43 | 129.89 | 192.59 | 194.79 | 279.9 | 404.0 | 414.5 | 54.98 | 24.59 | 13.98 | 27.42 | 40.78 | 41.61 |
| 10.00 | 139.08 | 212.54 | 216.35 | 285.5 | 429.4 | 435.7 | 57.63 | 26.10 | 14.71 | 27.87 | 42.46 | 44.36 |

[SC = Simple cycle; CRC= Conventional regeneration cycle; ARC=Alternative regeneration cycle]

Figure 6.1 represents the power vs. fuel flow ate for three cogeneration systems. Power output is marginally higher in ARC as compared to CRC system. Power output increases with fuel flow rate. Similar trends for specific power output are shown in Figure 6.2. Variation of cycle efficiency with fuel flow rate is given in Figure 6.3. Cycle efficiency is a strong function of compression ratio. In present case the rated compression ratio varies between 7.3 to 10.56 for given range of fuel flow rate. Therefore it can be expected that ARC system will show relatively better performance with higher compressor pressure ratio.

The cycle efficiency for simple cycle (SC), conventional regeneration (CRC) and alternative regeneration (ARC) are varying in the range of 20-27, 36-42 and 36-45 percent respectively. The Figure 6.3 indicates that the cycle efficiency is relatively higher in case of gas turbine cogeneration system with alternative regeneration.

Figure 6.1 Variation of power output with fuel flow rate

Figure 6.2 Variation in specific power output with Fuel flow rate

Figure 6.3 Variation of Cycle efficiency with Fuel flow rate

Figure 6.4 Performance of various cycles as a function of regenerator pressure drop

Figure 6.4 shows the variation of cycle efficiency with varying regenerator pressure drop for three systems. The regenerator effectiveness is taken as 0.9 and 0.7 in this Figure. The trend indicates that the cycle efficiency is maximum in case of gas turbine cogeneration system with alternative regeneration for the same pressure drop range. For regenerator effectiveness 0.7 the trend of graph is same.

Figure 6.5 Variation of Steam Generation Rate with Fuel flow rate

Comparison of steam generation in three systems is shown in Figure 6.5. Steam generation rate is least in the ARC system which is obvious due to higher cycle efficiency. Appendix C represents the mass flow rate, temperature, and pressure and enthalpy data for three types of cogeneration system for fuel flow rate equal to 6.23 kg /s.

CHAPTER 6

CONCLUSIONS AND SUGGESTIONS

FOR   FUTURE WORK

6.1 Conclusions

Above analysis based on simulation of gas turbine cogeneration system shows that alternative regeneration technique is beneficial to improve performance of the gas turbine cogeneration system. Following conclusions can be drawn for the present study

- For the same input condition the gas turbine cogeneration system with alternative regeneration shows better performance in terms of power output, specific power output and cycle efficiency.

- Cycle efficiency is a strong function of regenerator pressure drop.

6.2 Suggestion for future work

- An exhaustive parametric study with economic consideration is required for gas turbine cogeneration system with alternative regeneration.

- Inlet air cooling technologies should be incorporated with the system for further performance improvement.

REFERNECES

[1] Sung Hoon Hwang, Soo Hyoung Yoon, Tong Seop Kim, “Design and Off-Design

Characteristics of the Alternative Recuperated Gas Turbine Cycle with Divided Turbine Expansion”, Elsevier Science Ltd 129, 2006, Pp 428-436

[2] Paul A. Dellenback, “Improved gas turbine efficiency through Alternative Regenerator configuration”, Engineering for gas turbine and Power, Transaction of the ASME 124, 2002, Pp 441-46.

[3] T. Korakianitis, J. Grantstrom stide, F. Massardo, “Parametric Performance of Combined-Cogeneration Power Plants with Various Power and Efficiency Enhancements”, Elsevier Science Ltd 127, 1997, Pp 65-73

[4] Paul A. Dellenback, “A Reassessment of the Alternative Regeneration Cycle”, Engineering for gas turbine and Power, Transaction of the ASME 128, 2006, Pp 783-88.

[5] Stoecker W.F., “Design of thermal systems”, McGraw-hill, Third edition 1989, Pp 124-131, 331, 339-341.

[6] Seyedan B., Dhar P.L., Gaur R.R., Bindra G.S., “Simulation and optimization studies of a combined cycle power plant”, Thesis of doctor of philosophy, IIT Delhi,1995

[7] T. Chmielniak, W. Kosman , G. Kosman, “Simulation modules of thermal processes for performance control of CHP plant with a gas turbine unit,” Elsevier Science Ltd , 2005, Pp 2181–2187

[8] Y. G. Li, P. Pilidis, M. A. Newby, “An Adaptation Approach for Gas Turbine Design-Point Performance Simulation”, Engineering for gas turbine and Power, Transaction of the ASME 128, 2006, Pp786-793

[9] Francisco Sancho-Bastos, Horacio Perez-Blanco, “Cogeneration System Simulation

And Control to Meet Simultaneous Power, Heating, and Cooling Demands”, Elsevier Science Ltd 127, 2003, Pp 404-410

[10] Moran M.J., “Thermal System design and optimization”, Wiley-IEEE, 1996, Pp156-158,187-193,517-21

[11] Ravi Kumar N., Dr Rama Krishna K., “second law analysis of gas turbine power plant with alternative regeneration”, ISHMT, Heat and mass transfer conference 2006, Pp1813-18

[12] Chappell M.S. and Cockshutt E.P, “Gas Turbine Cycle Calculations”, National research Council Canada, 1974.

[13] Nag P. K., “power plant technology”, Tata McGraw-Hill, Second edition, Pp178, 214, and 860,861

[14] Roger and Cohen, “Gas turbine theory”, Wesley Longman, fourth edition 1998, Pp 28, 262

[15]  S. M Camporael, B.fortunato, M mastrovito, “A modular code for real time dynamic simulation of gas turbine in simulink” Engineering for gas turbine and Power, Transaction of the ASME 128,2006,Pp 506-17

[16]  V. Ramaprabhu, R.P. roy, “A computation model of a combined power generation unit” Engineering for gas turbine and Power, Transaction of the ASME 126,2004,Pp 231-36

[17] P. Bedont, O. Grillo, A. F. Massardo, “Off-Design Performance Analysis of a Hybrid System Based on an Existing Molten Fuel Cell Stack”;  Elsevier Science Ltd 125,  2002,Pp 986-994

[18] Bolesaw Zaporowski, Rados_aw Szczerbowski, “Energy analysis of technological systems of natural gas fired combined heat-and-power plants”, Elsevier Science Ltd 75, 2003, Pp 43-50

[19] Nobuyoshi Tsuzuki, Yasuyoshi Kato, Takao Ishiduka, “High performance printed circuit heat exchanger”, July 2006, Applied Thermal Engineering, Elsevier Science Ltd  27,2007, Pp 1702–1707

[20] S.H. Noie-Baghban, G.R. Majideia, “Waste heat recovery using heat pipe heat exchanger (HPHE) for surgery rooms in hospitals” , Applied Thermal Engineering, Elsevier Science Ltd 20, 2000, Pp 1271-1282.

[21] Nijaguna B. T., “Thermal science data book”, Tata McGraw hills, Pp 4.7-4.15, 4.35.

[22] Ryohei Yokoyama, Koichi Ito, “Optimal design of Gas turbine Cogeneration plants in consideration of discreetness of equipment capabilities”, Engineering for gas turbine and Power, Transaction of the ASME 128, 2006, Pp 336-43

[23] Felster S., Favrat D.,Von Spakovsky M.R., “The thermo economic analysis andenivironomic modeling and optimization of the synthesis and operation of combined cycle with advanced options”, Engineering for gas turbine and Power, Transaction of the ASME 123,2001,Pp 717-26

[24] Masumi IWAI, “Thermodynamic Table for Performance Calculations in Gas Turbine Engine”, Proceedings of the International Gas Turbine Congress 2003 Tokyo, November 2003, Pp 1-9.

[25] Ongiro A., Ugursal V. I., A1 Taweel and J. D. Walker, “Modeling of Heat Recovery Steam Generator Performance”, Applied Thermal Engineering Elsevier Science Ltd 17, 1997, Pp. 427-446

[26] Gay R.R., “Computer program analyzes gas turbine power plant”, Turbo machinery International, September 1988.

[27] Perz, E., “A computer method for thermal power cycle calculation”, Engineering for gas turbine and Power -Transaction of the ASME 112, April 1991, Pp. 184-189

APPENDIX A

Table A.1 Coefficients for thermodynamic functions used to calculate enthalpy and specific heat of substances [7]

| Symbol | T(250-800K) | T(800-2200K) |
| --- | --- | --- |
| Co | 1.0189 | 7.98632E-1 |
| C1 | -1.37836E-4 | 5.3392E-4 |
| C2 | 1.9843E-7 | -2.2881E-7 |
| C3 | 4.2399E-10 | 3.37420E-11 |
| C4 | -3.7632E-13 | 0.0000 |
| CH | -1.6984 | 4.7384E1 |
| CF | 9.1992E-1 | 2.0190 |
| CPo | -3.5949E-1 | 1.0887 |
| CP1 | 4.5163E-3 | -1.4158E-4 |
| CP2 | 2.8116E-6 | 1.9160E-6 |
| CP3 | -2.1708E-8 | -1.2400E-9 |
| CP4 | 2.8688E-11 | 3.0166E-13 |
| CP5 | -1.2226E-14 | -2.6117E-17 |
| Ho | 6.2637E1 | -1.7683E2 |
| H1 | -5.2903E-1 | 8.3690E-1 |
| H2 | 3.2226E-3 | 3.6476E-4 |
| H3 | -2.1670E-4 | 2.5155E-7 |
| H4 | 2.4951E-10 | -1.2441E-10 |
| H5 | 3.4891E-13 | 1.6406E-14 |
| Fo | -7.1259E-1 | -1.2645E0 |
| F1 | -2.2950E-4 | 4.4686E-3 |
| F2 | 1.3154E-5 | -2.8538E-6 |
| F3 | -2.5531E-8 | 1.6403E-9 |
| F4 | 2.2390E-11 | -5.3143E-13 |
| F5 | -7.6071E-15 | 6.9884E-17 |

Table A.2 Enthalpy of formation at 298K and 1 bar pressure ideal gas enthalpy of different gas [10]

|  | Oxygen O2 hf˚298=0 kJ/kmol M=32 | Carbondi oxide CO2 hf˚298= -393522 kJ/kmol M=44 | Carbon monoxide CO hf˚298= -110529l 0kJ/kmol M=28 | Water H2O hf˚298= -241827 kJ/kmol M=18 | Hydrogen H2 hf˚298= 0 kJ/kmol M=2 | Nitrogen N2 hf˚298= 0kJ/kmol M=28 |
| --- | --- | --- | --- | --- | --- | --- |
| T K | (h˚-h˚298) kJ/kmol | (h˚-h˚298) kJ/kmol | (h˚-h˚298) kJ/kmol | (h˚-h˚298) kJ/kmol | (h˚-h˚298) kJ/kmol | (h˚-h˚298) kJ/kmol |
| 298 | 0 | 0 | 0 | 0 | 0 | 0 |
| 900 | 19246 | 28014 | 18397 | 21924 | 17682 | 18221 |
| 1000 | 22707 | 33405 | 21686 | 25978 | 20686 | 21406 |
| 1100 | 26217 | 28894 | 25033 | 30167 | 23723 | 24757 |
| 1200 | 29765 | 44484 | 28426 | 34476 | 26794 | 28108 |
| 1300 | 33351 | 50158 | 31865 | 38903 | 29907 | 31501 |
| 1400 | 36966 | 55907 | 25338 | 43447 | 33062 | 34936 |

APPENDIX B

Table B.1 Mass flow rate, Temperature, Pressure and enthalpy data for gas turbine cogeneration system

[Mass flow rate of fuel = 6.23 kg/s]

| Points | Substance | Mass flow rate Kg/s | Temperature K | Press Bar | Enthalpy kJ/kg |
| --- | --- | --- | --- | --- | --- |
| 1 | Air | 347.58 | 300.00 | 1.013 | 299.37 |
| 2 | Air | 347.58 | 597.12 | 7.301 | 591.35 |
| 3 | Combustion gases | 353.81 | 1207.01 | 7.117 | 1288.15 |
| 4 | Combustion gases | 353.81 | 790.12 | 1.038 | 801.23 |
| 5 | Combustion gases | 353.81 | 421.00 | 1.013 | 485.20 |
| 6 | Water | 41.50 | 298.15 | 1.013 | 104.89 |
| 7 | Steam | 41.50 | 485.55 | 20.00 | 2279.5 |
| 8 | Combustion gases | 353.81 | - | - | - |
| 9 | Combustion gases | 353.81 | - | - | - |
| 10 | Combustion gases | 353.81 | - | - | - |

Table B.2 Mass flow rate, Temperature, Pressure and enthalpy data for gas turbine cogeneration system with regeneration

[Mass flow rate of fuel = 6.23 kg/s]

| Points | Substance | Mass flow rate Kg/s | Temperature K | Press Bar | Enthalpy kJ/kg |
| --- | --- | --- | --- | --- | --- |
| 1 | Air | 351.27 | 300.00 | 1.013 | 299.37 |
| 2 | Air | 351.27 | 599.22 | 7.329 | 592.61 |
| 3 | Combustion gases | 357.50 | 1287.10 | 6.969 | 1460.01 |
| 4 | Combustion gases | 357.50 | 978.01 | 1.064 | 901.30 |
| 5 | Combustion gases | 357.50 | 421.50 | 1.013 | 485.20 |
| 6 | Water | 18.74 | 298.150 | 1.013 | 104.89 |
| 7 | Steam | 18.74 | 485.50 | 20.00 | 2799.21 |
| 8 | Combustion gases | 357.50 | 758.58 | 7.158 | 871.23 |
| 9 | Combustion gases | 357.50 | 538.36 | 2.561 | 626.34 |
| 10 | Combustion gases | - | - | - | - |

Table C.3 Mass flow rate, Temperature, Pressure and enthalpy data for gas turbine cogeneration system with alternative regeneration

[Mass flow rate of fuel = 6.23 kg/s]

| Points | Substance | Mass flow rate Kg/s | Temperature K | Press Bar | Enthalpy kJ/kg |
| --- | --- | --- | --- | --- | --- |
| 1 | Air | 366.67 | 300.00 | 1.013 | 299.37 |
| 2 | Air | 366.67 | 605.61 | 7.329 | 605.37 |
| 3 | Combustion gases | 372.9 | 1312.5 | 6.990 | 1508.90 |
| 4 | Combustion gases | 372.9 | 1036.1 | 2.625 | 1206.82 |
| 5 | Combustion gases | 372.9 | 421.00 | 1.013 | 485.20 |
| 6 | Water | 9.45 | 298.150 | 1.013 | 104.89 |
| 7 | Steam | 9.45 | 485.50 | 20 | 2799.21 |
| 8 | Combustion gases | 372.9 | 979.20 | 7.158 | 1146.4 |
| 9 | Combustion gases | 372.9 | 721.58 | 2.561 | 829.8 |
| 10 | Combustion gases | 372.9 | 489.02 | 1.0383 | 554.1 |

APPENDIX C

Newton Rapsons Methodology to solve the non linear equations

Newton method approximates any given f(x) by a linear function (linear model); solves the linear model to get a new guess.

Derivations:  Expand f(x) using Taylor Series:  f(x) = f(xk) + f'(xk)(x-xk)

At the solution f(x) = 0 = f(xk) + f'(xk)(x-xk)

| Rearranging: |  |
| --- | --- |

Multi-dimensional case for Newton-Rapsons Method:

|  | Talyor Series of m functions with n variables: |  |  |
| --- | --- | --- | --- |
|  | where |  |  |
|  | J= |  |  |
|  | with m = n | Set |  |

Advantages and Disadvantages:

a. The method is very expensive - It needs the function evaluation and then the derivative evaluation. If the tangent is parallel or nearly parallel to the x-axis, then the method does not converge.

b. Usually Newton method is expected to converge only near the solution.

c. The advantage of the method is its order of convergence is quadratic.

d. Convergence rate is one of the fastest when it does converges

When Newton's Method does not converge:

Rewrite as:     , where

k - is a scalar parameter which is adjusted to either less than 1 or more than 1 (=1 is the original Newton method) to force convergence.

Nonlinear System of Equations:

Recall that the Newton equation for nonlinear equation is:

where J is the numerical Jacobian matrix calculated at every iteration using the current solution xk.  The above equation can be modified such that there is no need for an inverse (inverse costs twice as much to solve as the following)

where correction step sk is calculated by solving

To solve a system of nonlinear equations using Newton method, in each iteration we solve a system of linear equations using the current Jacobian matrix.

# Jacobian Matrix

A function f=f(x) of one variable is differentiable at x with derivative if

This definition can be generalized to the case of m functions of n variables. Then x and h are matrices (n-vectors), f and R are matrices, and one defines for example

then becomes an matrix, called the Jacobian matrix whose elements are the partial derivatives:

Other possible notations for are:

The chain rule is valid in its usual form. If  then  . Note that this is a matrix product, and therefore non-commutative except in special cases. In terms of matrix elements,

A coordinate transformation is an important special case, with p=n, and with u=u(x) the inverse transformation of x=x(u). That is, u=u(x) = u(x(u)), and by the chain rule