## Sheet6
Table 4.1 PERFORMANCE OF CASCADE REFRIGERATION SYSTEM , DATA RELATED TO WORK DONE & COEFFICIENT OF PEFORMANCE
Sl No. | Stage-I |  | Stage-II |  | Stage-III |  | Refrigeration Effect | Power (KW) |  |  | Total Power(KW) | COP |  |  | COP
| Condenser Temp(°C) | Evaporator Temp(°C) | Condenser Temp (°C) | Evaporator Temp(°C) | Condenser Temp (°C) | Evaporator Temp(°C) |  | stage I | Stage -II | Stage -III |  | stage I | stage II | stage III
Effect of increase in condenser Temperature
1 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 7.317 | 11.008 | 11.995 | 30.32 | 7.949 | 4.284 | 2.931 | 1.16
2 | 35 | 0 | 5 | -40 | -35 | -85 | 10 TR | 8.821 | 11.008 | 11.995 | 31.824 | 6.609 | 4.284 | 2.931 | 1.105
3 | 40 | 0 | 5 | -40 | -35 | -85 | 10 TR | 10.566 | 11.008 | 11.995 | 33.564 | 5.504 | 4.284 | 2.931 | 1.0477
Effect of decrease in Evaporator Temperature
4 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 7.317 | 11.008 | 11.995 | 30.32 | 7.949 | 4.284 | 2.931 | 1.16
5 | 30 | -5 | 5 | -40 | -35 | -85 | 10 TR | 8.905 | 11.008 | 11.995 | 31.908 | 6.531 | 4.284 | 2.931 | 1.102
6 | 30 | -10 | 5 | -40 | -35 | -85 | 10 TR | 10.608 | 11.008 | 11.995 | 33.606 | 5.483 | 4.284 | 2.931 | 1.046
7 | 30 | -15 | 5 | -40 | -35 | -85 | 10 TR | 12.456 | 11.008 | 11.995 | 35.459 | 4.669 | 4.284 | 2.931 | 0.9917
Effect of increase of condenser Temperature in cascade Heat exchanger-I
8 | 30 | 0 | 0 | -40 | -35 | -85 | 10 TR | 7.128 | 9.504 | 11.995 | 28.627 | 7.949 | 4.284 | 2.931 | 1.228
9 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 7.317 | 11.008 | 11.995 | 30.32 | 7.949 | 4.284 | 2.931 | 1.16
10 | 30 | 0 | 10 | -40 | -35 | -85 | 10 TR | 7.51 | 12.548 | 11.995 | 32.053 | 7.949 | 3.758 | 2.931 | 1.097
11 | 30 | 0 | 15 | -40 | -35 | -85 | 10 TR | 7.733 | 14.25 | 11.995 | 33.978 | 7.949 | 3.312 | 2.931 | 1.035
Effect of decrease in Evaporator Temperature in Cascade Heat Exchanger _ I
12 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 7.317 | 11.008 | 11.995 | 30.32 | 7.949 | 4.284 | 2.931 | 1.16
13 | 30 | 0 | 5 | -45 | -35 | -85 | 10 TR | 7.534 | 12.735 | 11.995 | 32.264 | 7.949 | 3.703 | 2.931 | 1.09
14 | 30 | 0 | 5 | -50 | -35 | -85 | 10 TR | 7.774 | 14.604 | 11.995 | 34.373 | 7.949 | 3.221 | 2.931 | 1.023
Effect of increase of condenser Temperature in cascade Heat exchanger-II
15 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 7.317 | 11.008 | 11.995 | 30.32 | 7.949 | 4.284 | 2.931 | 1.16
16 | 30 | 0 | 5 | -40 | -30 | -85 | 10 TR | 7.571 | 11.389 | 13.63 | 32.59 | 7.949 | 4.284 | 2.58 | 1.079
17 | 30 | 0 | 5 | -40 | -25 | -85 | 10 TR | 7.842 | 11.798 | 15.38 | 35.02 | 7.949 | 4.284 | 2.286 | 1.004
Effect of decrease in Evaporator Temperaturein Cascade Heat Exchanger -II
18 | 30 | 0 | 5 | -40 | -35 | -75 | 10 TR | 6.808 | 10.203 | 8.666 | 25.677 | 7.949 | 4.284 | 4.057 | 1.369
19 | 30 | 0 | 5 | -40 | -35 | -80 | 10 TR | 7.052 | 10.567 | 10.243 | 27.862 | 7.949 | 4.284 | 3.432 | 1.262
20 | 30 | 0 | 5 | -40 | -35 | -85 | 10TR | 7.317 | 11.008 | 11.995 | 30.32 | 7.949 | 4.284 | 2.931 | 1.16
21 | 30 | 0 | 5 | -40 | -35 | -88.8 | 10 TR | 7.555 | 11.312 | 13.43 | 32.298 | 7.949 | 4.284 | 2.618 | 1.089
86

## Sheet7
Table 4.2 PERFORMANCE OF CASCADE REFRIGERATION SYSTEM , DATA RELATED TO COMPRESSOR DISCHARGE TEMPERATURE , PRESSURE RATIO AND SPECIFIC VOLUME
Sl No. | Stage-I |  | Stage-II |  | Stage-III |  | Refrigeration Effect | Compressor descharge Temp (°C) |  |  | Pressure Ratio |  |  | Specific Volume (m3/kg)
| Condenser Temp(°C) | Evaporator Temp(°C) | Condenser Temp (°C) | Evaporator Temp(°C) | Condenser Temp (°C) | Evaporator Temp(°C) |  | Compr -I | Compr -II | Compr -III | Stage-I | Stage-II | Stage-III | v1 | v2 | v3
Effect of increase in condenser Temperature
1 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 30 | 16.9 | 5.6 | 2.585 | 4.964 | 7.454 | 0.2356 | 0.3799 | 0.4084
2 | 35 | 0 | 5 | -40 | -35 | -85 | 10 TR | 35 | 16.9 | 5.6 | 2.972 | 4.964 | 7.454 | 0.2353 | 0.3799 | 0.4084
3 | 40 | 0 | 5 | -40 | -35 | -85 | 10 TR | 40 | 16.9 | 5.6 | 3.389 | 4.964 | 7.454 | 0.2353 | 0.3799 | 0.4084
Effect of decrease in Evaporator Temperature
4 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 30 | 16.9 | 5.6 | 2.585 | 4.964 | 7.454 | 0.2356 | 0.3799 | 0.4084
5 | 30 | -5 | 5 | -40 | -35 | -85 | 10 TR | 30 | 16.9 | 5.6 | 3.096 | 4.964 | 7.454 | 0.2789 | 0.3799 | 0.4084
6 | 30 | -10 | 5 | -40 | -35 | -85 | 10 TR | 30 | 16.9 | 5.6 | 3.741 | 4.964 | 7.454 | 0.3329 | 0.3799 | 0.4084
7 | 30 | -15 | 5 | -40 | -35 | -85 | 10 TR | 30 | 16.9 | 5.6 | 4.558 | 4.964 | 7.454 | 0.40031 | 0.3799 | 0.4084
Effect of increase of condenser Temperature in cascade Heat exchanger-I
8 | 30 | 0 | 0 | -40 | -35 | -85 | 10 TR | 30 | 11.16 | 5.6 | 2.585 | 4.275 | 7.454 | 0.2356 | 0.3799 | 0.4084
9 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 30 | 16.9 | 5.6 | 2.585 | 4.964 | 7.454 | 0.2356 | 0.3799 | 0.4084
10 | 30 | 0 | 10 | -40 | -35 | -85 | 10 TR | 30 | 22.5 | 5.6 | 2.585 | 5.737 | 7.454 | 0.2356 | 0.3799 | 0.4084
11 | 30 | 0 | 15 | -40 | -35 | -85 | 10 TR | 30 | 28.03 | 5.6 | 2.585 | 6.592 | 7.454 | 0.2356 | 0.3799 | 0.4084
Effect of decrease in Evaporator Temperature in Cascade Heat Exchanger _ I
12 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 30 | 16.9 | 5.6 | 2.585 | 4.964 | 7.454 | 0.2356 | 0.3799 | 0.4084
13 | 30 | 0 | 5 | -45 | -35 | -85 | 10 TR | 30 | 19.18 | 5.6 | 2.585 | 6.198 | 7.454 | 0.2356 | 0.4669 | 0.4084
14 | 30 | 0 | 5 | -50 | -35 | -85 | 10 TR | 30 | 21.74 | 5.6 | 2.585 | 7.824 | 7.454 | 0.2356 | 0.5796 | 0.4084
Effect of increase of condenser Temperature in cascade Heat exchanger-II
15 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 30 | 16.9 | 5.6 | 2.585 | 4.964 | 7.454 | 0.2356 | 0.3799 | 0.4084
16 | 30 | 0 | 5 | -40 | -30 | -85 | 10 TR | 30 | 16.9 | 13.51 | 2.585 | 4.964 | 8.693 | 0.2356 | 0.3799 | 0.4084
17 | 30 | 0 | 5 | -40 | -25 | -85 | 10 TR | 30 | 16.9 | 21.14 | 2.585 | 4.964 | 10.071 | 0.2356 | 0.3799 | 0.4084
Effect of decrease in Evaporator Temperaturein Cascade Heat Exchanger -II
18 | 30 | 0 | 5 | -40 | -35 | -75 | 10 TR | 30 | 16.888 | -5.42 | 2.58 | 4.96 | 4.5715 | 0.2356 | 0.3799 | 0.25923
19 | 30 | 0 | 5 | -40 | -35 | -80 | 10 TR | 30.009 | 16.888 | -0.17 | 2.58 | 4.96 | 5.797 | 0.2356 | 0.3799 | 0.3234
20 | 30 | 0 | 5 | -40 | -35 | -85 | 10TR | 30 | 16.9 | 5.6 | 2.585 | 4.964 | 7.454 | 0.2356 | 0.3799 | 0.4084
21 | 30 | 0 | 5 | -40 | -35 | -88.8 | 10 TR | 30.009 | 16.888 | 10.317 | 2.583 | 4.966 | 9.111 | 0.2356 | 0.38 | 0.4919
87

## Sheet5
Table 4.3 PERFORMANCE OF CASCADE REFRIGERATION SYSTEM , DATA RELATED TO MASS FLOW RATE SIZE OF BORE AND STROKE LENGTH
Sl No. | Stage-I |  | Stage-II |  | Stage-III |  | Refrigeration Effect | Mass flow rate in stage (Kg/min) |  |  | Stage I |  | Stage II |  | Stage III
| Condenser Temp(°C) | Evaporator Temp(°C) | Condenser Temp (°C) | Evaporator Temp(°C) | Condenser Temp (°C) | Evaporator Temp(°C) |  | m1 | m2 | m3 | Bore (in mm) | Stroke lengh (in mm) | Bore (in mm) | Stroke lengh (in mm) | Bore (in mm) | Stroke lengh (in mm)
Effect of increase in condenser Temperature
1 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 12.302 | 8.974 | 5.958 | 154 | 185 | 163 | 196 | 145 | 174
2 | 35 | 0 | 5 | -40 | -35 | -85 | 10 TR | 12.89 | 8.974 | 5.958 | 154 | 185 | 163 | 196 | 145 | 174
3 | 40 | 0 | 5 | -40 | -35 | -85 | 10 TR | 13.537 | 8.974 | 5.958 | 159 | 191 | 163 | 196 | 145 | 174
Effect of decrease in Evaporator Temperature
4 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 12.302 | 8.974 | 5.958 | 154 | 185 | 163 | 196 | 145 | 174
5 | 30 | -5 | 5 | -40 | -35 | -85 | 10 TR | 12.62 | 8.974 | 5.958 | 164 | 197 | 163 | 196 | 145 | 174
6 | 30 | -10 | 5 | -40 | -35 | -85 | 10 TR | 12.932 | 8.974 | 5.958 | 176 | 212 | 163 | 196 | 145 | 174
7 | 30 | -15 | 5 | -40 | -35 | -85 | 10 TR | 13.259 | 8.974 | 5.958 | 188 | 226 | 163 | 196 | 145 | 174
Effect of increase of condenser Temperature in cascade Heat exchanger-I
8 | 30 | 0 | 0 | -40 | -35 | -85 | 10 TR | 11.983 | 8.617 | 5.958 | 153 | 184 | 160 | 192 | 145 | 174
9 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 12.302 | 8.974 | 5.958 | 154 | 185 | 163 | 196 | 145 | 174
10 | 30 | 0 | 10 | -40 | -35 | -85 | 10 TR | 12.627 | 9.345 | 5.958 | 155 | 186 | 165 | 198 | 145 | 174
11 | 30 | 0 | 15 | -40 | -35 | -85 | 10 TR | 13 | 9.779 | 5.958 | 157 | 189 | 167 | 201 | 145 | 174
Effect of decrease in Evaporator Temperature in Cascade Heat Exchanger _ I
12 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 12.302 | 8.974 | 5.958 | 154 | 185 | 163 | 196 | 145 | 174
13 | 30 | 0 | 5 | -45 | -35 | -85 | 10 TR | 12.666 | 9.137 | 5.958 | 156 | 188 | 175 | 210 | 145 | 174
14 | 30 | 0 | 5 | -50 | -35 | -85 | 10 TR | 13.07 | 9.3175 | 5.958 | 157 | 189 | 189 | 227 | 145 | 174
Effect of increase of condenser Temperature in cascade Heat exchanger-II
15 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 12.302 | 8.974 | 5.958 | 154 | 185 | 163 | 196 | 145 | 174
16 | 30 | 0 | 5 | -40 | -30 | -85 | 10 TR | 12.728 | 9.285 | 6.209 | 156 | 188 | 164 | 197 | 147 | 177
17 | 30 | 0 | 5 | -40 | -25 | -85 | 10 TR | 13.184 | 9.618 | 6.487 | 158 | 190 | 166 | 200 | 149 | 179
Effect of decrease in Evaporator Temperaturein Cascade Heat Exchanger -II
18 | 30 | 0 | 5 | -40 | -35 | -75 | 10 TR | 11.446 | 8.331 | 5.786 | 150 | 180 | 159 | 191 | 124 | 149
19 | 30 | 0 | 5 | -40 | -35 | -80 | 10 TR | 11.855 | 8.629 | 5.868 | 152 | 183 | 166 | 200 | 134 | 161
20 | 30 | 0 | 5 | -40 | -35 | -85 | 10TR | 12.302 | 8.974 | 5.958 | 154 | 185 | 163 | 196 | 145 | 174
21 | 30 | 0 | 5 | -40 | -35 | -88.8 | 10 TR | 12.6909 | 9.2369 | 6.029 | 156 | 188 | 164 | 197 | 155 | 186
88

## Sheet2
Table 4.4 SECOND LAW EFFICIENCY AND EXERGY DISTRATACTION OF CASCADE REFRIGERATION SYSTEM
Sl No. | Stage-I |  | Stage-II |  | Stage-III |  | Refrigeration Effect | COP (Carnot) |  |  |  | II nd law Efficiency |  |  |  | Exergy Destruction ( KW)
| Condenser Temp(°C) | Evaporator Temp(°C) | Condenser Temp (°C) | Evaporator Temp(°C) | Condenser Temp (°C) | Evaporator Temp(°C) |  | stage I | Stage -II | Stage -III | System | stage I | stage II | stage III | System | stage I | stage II | stage III | System
Effect of increase in condenser Temperature
1 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 9.1 | 5.177 | 3.76 | 1.637 | 87.35 | 82.73 | 77.95 | 70.96 | 0.9256 | 1.9018 | 2.6449 | 8.8049
2 | 35 | 0 | 5 | -40 | -35 | -85 | 10 TR | 7.8 | 5.177 | 3.76 | 1.5667 | 84.73 | 82.73 | 77.95 | 70.53 | 1.3469 | 1.9018 | 2.6449 | 9.3785
3 | 40 | 0 | 5 | -40 | -35 | -85 | 10 TR | 6.825 | 5.177 | 3.76 | 1.504 | 80.64 | 82.73 | 77.95 | 69.66 | 2.0455 | 1.9018 | 2.6449 | 10.1833
Effect of decrease in Evaporator Temperature
4 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 9.1 | 5.177 | 3.76 | 1.6347 | 87.35 | 82.73 | 77.95 | 70.96 | 0.9256 | 1.9018 | 2.6449 | 8.8049
5 | 30 | -5 | 5 | -40 | -35 | -85 | 10 TR | 7.657 | 5.177 | 3.76 | 1.6347 | 85.29 | 82.73 | 77.95 | 67.41 | 1.3099 | 1.9018 | 2.6449 | 10.3988
6 | 30 | -10 | 5 | -40 | -35 | -85 | 10 TR | 6.575 | 5.177 | 3.76 | 1.6347 | 83.39 | 82.73 | 77.95 | 63.98 | 1.7691 | 1.9018 | 2.6449 | 12.1048
7 | 30 | -15 | 5 | -40 | -35 | -85 | 10 TR | 5.733 | 5.177 | 3.76 | 1.6347 | 81.43 | 82.73 | 77.95 | 60.66 | 2.313 | 1.9018 | 2.6449 | 13.9495
Effect of increase of condenser Temperature in cascade Heat exchanger-I
8 | 30 | 0 | 0 | -40 | -35 | -85 | 10 TR | 9.1 | 5.825 | 3.76 | 1.6347 | 87.35 | 85.16 | 77.95 | 75.12 | 0.9088 | 1.4107 | 2.6449 | 7.1224
9 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 9.1 | 5.177 | 3.76 | 1.6347 | 87.35 | 82.73 | 77.95 | 70.96 | 0.9256 | 1.9018 | 2.6449 | 8.804
10 | 30 | 0 | 10 | -40 | -35 | -85 | 10 TR | 9.1 | 4.66 | 3.76 | 1.6347 | 87.35 | 80.64 | 77.95 | 67.1 | 0.95 | 2.4293 | 2.6449 | 10.5454
11 | 30 | 0 | 15 | -40 | -35 | -85 | 10 TR | 9.1 | 4.236 | 3.76 | 1.6347 | 87.35 | 78.18 | 77.95 | 64.53 | 0.9782 | 3.1093 | 2.6449 | 12.052
Effect of decrease in Evaporator Temperature in Cascade Heat Exchanger _ I
12 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 9.1 | 5.177 | 3.76 | 1.6347 | 87.35 | 82.73 | 77.95 | 70.96 | 0.9256 | 1.9018 | 2.6449 | 8.8049
13 | 30 | 0 | 5 | -45 | -35 | -85 | 10 TR | 9.1 | 4.56 | 3.76 | 1.6347 | 87.35 | 81.2 | 77.95 | 66.67 | 0.953 | 2.3941 | 2.6449 | 10.7536
14 | 30 | 0 | 5 | -50 | -35 | -85 | 10 TR | 9.1 | 4.0545 | 3.76 | 1.6347 | 87.35 | 79.44 | 77.95 | 62.58 | 0.9834 | 2.7455 | 2.6449 | 12.6823
Effect of increase of condenser Temperature in cascade Heat exchanger-II
15 | 30 | 0 | 5 | -40 | -35 | -85 | 10 TR | 9.1 | 5.177 | 3.76 | 1.6347 | 87.35 | 82.73 | 77.95 | 70.96 | 0.9256 | 1.9018 | 2.6449 | 8.8049
16 | 30 | 0 | 5 | -40 | -30 | -85 | 10 TR | 9.1 | 5.177 | 3.418 | 1.6347 | 87.35 | 82.73 | 75.47 | 66.005 | 0.9577 | 1.9667 | 3.3434 | 11.0806
17 | 30 | 0 | 5 | -40 | -25 | -85 | 10 TR | 9.1 | 5.177 | 3.133 | 1.6347 | 87.35 | 82.73 | 72.95 | 61.41 | 0.992 | 2.0375 | 4.1603 | 13.5412
Effect of decrease in Evaporator Temperaturein Cascade Heat Exchanger -II
18 | 30 | 0 | 5 | -40 | -35 | -75 | 10 TR | 9.1 | 5.177 | 4.95 | 1.6347 | 87.35 | 82.73 | 81.96 | 83.74 | 0.8612 | 1.762 | 1.5615 | 7.038
19 | 30 | 0 | 5 | -40 | -35 | -80 | 10 TR | 9.1 | 5.177 | 4.288 | 1.6347 | 87.35 | 82.73 | 80.03 | 77.2 | 0.892 | 1.8249 | 2.0465 | 7.8208
20 | 30 | 0 | 5 | -40 | -35 | -85 | 10TR | 9.1 | 5.177 | 3.76 | 1.635 | 87.35 | 82.73 | 77.95 | 70.96 | 0.9256 | 1.9018 | 2.6449 | 8.8049
21 | 30 | 0 | 5 | -40 | -35 | -88.8 | 10 TR |  | 5.177 | 3.428 | 1.5505 | 87.35 | 82.73 | 76.37 | 70.23 | 0.9557 | 1.9536 | 3.1735 | 9.6151
89