PERFORMANCE EVALUATION OF ASP BASED 16 MGD SEWAGE TREATMENT PLANT AT OKHLA, DELHI

A DISSERTATION

SUBMITTED IN PARTIAL FULFILLMENT OF THE REQUIREMENTS

FOR THE AWARD OF THE DEGREE OF

MASTER OF ENGINEERING IN

CIVIL ENGINEERING (ENVIRONMENTAL ENGINEERING)

BY

VIJAY  KUMAR GUPTA

(Roll No. 4553)

Under the Guidance of

Prof. (Dr.) S. K. SINGH

Department of Civil and Environmental Engineering

Delhi College of Engineering

Delhi University, Delhi-110042

December, 2006

Department of Civil and Environmental Engineering

Delhi College of Engineering

Delhi University, Delhi-110042

CERTIFICATE

This is to certify that the dissertation titled “Performance Evaluation of ASP based 16 MGD  Sewage  Treatment  Plant  at  Okhla,  Delhi”, which is being submitted by Vijay Kumar Gupta, in partial fulfillment of the requirements for the award of degree of Master of Engineering in Civil Engineering (Environmental Engineering), is a bonafide record of his own work carried out by him under my guidance and supervision.

The matter embodied in this project has not been submitted for the award of any other degree.

Dr. S. K. Singh

Professor  & Head

Department of Civil & Environmental Engineering 						         Delhi College of Engineering

Delhi University, Delhi

Acknowledgement

I express my respectful gratitude to Dr. S. K. Singh, Professor & Head, Department of Environmental Engineering, Delhi College of Engineering for providing continuous valuable guidance, support and putting his trust in my abilities which motivated me to complete the project successfully.

I am highly indebted to Sh. V.S. Thind, Director (Projects) Sewerage, Delhi Jal Board for his suggestions, support and for permitting me to take time out of busy office schedule for completing the project.

I am thankful to all the staff members of Okhla Sewage Treatment Plant for providing me all the relevant data for the study, especially Sh. R.K. Gupta, Executive Engineer (E&M), Delhi Jal Board, who not only explained the working of the entire sewage treatment plant in minutest detail but also provided technical inputs as and when required.

My special thanks are due to Smt. Sangeeta Soni, Stenographer, Delhi Jal Board, who typed the manuscripts nicely and Sh. Devi Singh, who prepared the drawings on AutoCAD.

Thanks are also due to my cousin Sh. Suraj Aggarwal, D.G.M., Consulting Engineering Services and my colleagues in Delhi Jal Board for their constant encouragement.

I am always thankful and express my heartfelt feeling for my parents who had been inspiring and guiding me throughout the period of the course.  I am thankful to them from the core of my heart.

I am also thankful to my wife Smt. Anuradha and children Anuprea, Veenupriya and Vinayak who constantly encouraged me and allowed me to take out prime time for the project, which otherwise I would have spent with them.

I would also like to thank my classmate Sh. Anwer Sayeed for his constant support and encouragement.

Vijay Kumar Gupta

Abstract

Waste water is generated by every day human activities and various industrial processes.  If waste water is discharged untreated into water bodies it will result in large scale contamination of water sources and degradation of the eco-system.  Several waste water treatment processes have been developed over the time.  However, activated sludge process treatment of waste water is the oldest and still the most commonly used method.

The activated sludge process is an aerobic treatment process which converts non-settleable substances in finally divided, colloidal and dissolved form into a biological floc or activated sludge.  The activated sludge waste water treatment process is capable of producing an excellent effluent quality, but the performance of the plant is severely affected by characteristics of the influent, environment in the aeration basin and operating conditions within the secondary clarifier.  Best way to monitor the performance of an ASP based treatment plant is to constantly monitor the characteristics of raw sewage and the parameters of the effluent after each treatment unit such as primary clarifier, aeration basin and secondary clarifier.  The overall efficiency of the plant is limited by the maximum operational efficiency of the unit processes.

The purpose of this project is to assess the efficacy of activated sludge process treatment of waste water by studying the performance of an ASP based sewage treatment plant.  The assessment was directed at determining the characteristics of raw sewage and removal of pollutants during treatment by various units so as to evaluate the efficiency of the units.  The final quality of the effluent, in terms of Biochemical Oxygen Demand, Chemical Oxygen Demand, Suspended Solids etc., from the plant is the indicator of performance of the plant.

Contents

|  |  |  | Page No. |
| --- | --- | --- | --- |
| CERTIFICATE ACKNOWLEDGEMENT ABSTRACT CONTENTS LIST OF TABLES LIST OF FIGURES LIST OF PICTURES |  |  | i |
|  |  |  | ii |
|  |  |  | iii |
|  |  |  | iv |
|  |  |  | viii |
|  |  |  | x |
|  |  |  | xii |
| ABBREVIATIONS AND ACRONYMS |  |  | xiii |
| Chapter 1 | INTRODUCTION |  | 1 |
|  | 1.1 General |  | 1 |
|  | ## 1.2 Objective of Wastewater Treatment |  | 1 |
|  | ## 1.3 Wastewater Treatment Processes |  | 2 |
|  | ### Preliminary treatment |  | 2 |
|  | ### 1.3.2 Primary treatment |  | 2 |
|  | ### 1.3.3 Secondary treatment |  | 3 |
|  | ### 1.3.4 Tertiary (Advanced) treatment |  | 3 |
|  | 1.4 Scope and Objectives of the Study |  | 4 |
|  | 1.4.1 Scope |  | 4 |
|  | 1.4.2 Objectives |  | 4 |
| Chapter 2 | LITERATURE REVIEW |  | 5 |
| Chapter 3 | ACTIVATED SLUDGE PROCESS |  | 13 |
|  | 3.1 Activated Sludge Process |  | 13 |
|  | 3.2 Process Kinetics |  | 13 |
|  | 3.3 Design Considerations |  | 16 |
|  | 3.4 Factors Affecting Performance |  | 16 |
|  | 3.4.1 Influent characteristics |  | 17 |
|  | 3.4.1.1 Organic and Hydraulic Loading |  | 17 |
|  | 3.4.1.2 Effect of Toxic Substances |  | 17 |
|  | 3.4.2 Aeration basin environment |  | 17 |
|  | 3.4.2.1 Food and Dissolved Oxygen |  | 17 |
|  | 3.4.2.2 Adequate Mixing |  | 18 |
|  | 3.4.2.3 Correct F:M |  | 18 |
|  | 3.4.3 Secondary clarifier conditions |  | 19 |
|  | 3.4.3.1 Clarifier design features |  | 19 |
|  | 3.4.3.2 RAS flow rate |  | 20 |
|  | 3.5 Control Strategies |  | 20 |
|  | 3.5.1 MLSS and MLVSS Concentration |  | 20 |
|  | 3.5.2 Sludge Volume Index (SVI) |  | 21 |
|  | 3.5.3 Mean Cell Residence Time (MCRT) |  | 22 |
|  | 3.6 Typical Activated Sludge Wastewater Treatment |  | 24 |
| Chapter 4 | METHODOLOGY FOR PERFORMANCE EVALUATION OF SEWAGE TREATMENT PLANTS |  | 25 |
|  | 4.1 Performance evaluation |  | 25 |
|  | 4.2 Methodology |  | 25 |
|  | 4.2.1 Collection of plant data, Raw sewage characteristics and Desired effluent quality |  | 25 |
|  | - Monitoring of Inflow |  | 27 |
|  | 4.2.3 Collection of sample |  | 28 |
|  | 4.2.4 Analysis of samples |  | 29 |
|  | 4.2.5 Study Performance of Units |  | 29 |
|  | 4.2.5.1 Screen |  | 29 |
|  | 4.2.5.2 Grit Chamber (Detritus Tank) |  | 29 |
|  | 4.2.5.3 Primary Sedimentation Tank |  | 29 |
|  | 4.2.5.4 Aeration Tank |  | 30 |
|  | 4.2.5.5 Secondary Sedimentation Tank |  | 30 |
|  | 4.2.5.6 Effluent Quality |  | 30 |
|  | 4.3 Performance Evaluation Report |  | 30 |
| Chapter 5 | EVALAUTION OF PERFORMANCE OF 16 MGD SEWAGE TREATMENT PLANT |  | 31 |
|  | - General |  | 31 |
|  | - Description of 16 MGD Sewage Treatment Plant |  | 32 |
|  | 5.2.1 Bar Screen |  | 32 |
|  | 5.2.2 Grit Chamber (Detritor) |  | 33 |
|  | 5.2.3 Primary Clarifier |  | 33 |
|  | 5.2.4 Aeration Tank |  | 34 |
|  | 5.2.5 Secondary Clarifier |  | 34 |
|  | 5.2.6 Return Sludge Pumps |  | 34 |
|  | 5.2.7 Raw Sludge Pumps |  | 34 |
|  | 5.2.8 Digester |  | 34 |
|  | 5.2.9 Sludge Drying Beds |  | 35 |
|  | 5.3 Basic Design Criteria |  | 35 |
|  | 5.3.1 Flows |  | 35 |
|  | 5.3.2 Raw Sewage Characteristics |  | 36 |
|  | - Treated Sewage (Effluent) Characteristics |  | 36 |
|  | - Hydraulic Levels |  | 36 |
|  | - Basis of Unit Sizing |  | 36 |
|  | - Mechanically Cleaned Bar Screen |  | 36 |
|  | - Grit Removal |  | 37 |
|  | 5.4.3 Primary Clarifiers |  | 37 |
|  | 5.4.4 Aeration Tank |  | 37 |
|  | 5.4.5 Secondary Clarifiers |  | 38 |
|  | 5.4.6 Digesters |  | 38 |
|  | 5.4.7 Gas Holder |  | 38 |
|  | 5.4.8 Sludge Drying Beds |  | 38 |
|  | - Raw Sludge Sump cum Pump House |  | 39 |
|  | - Return Sludge Sump cum Pump House |  | 39 |
|  | 5.4.11 Filtrate Sump cum Pump House |  | 39 |
|  | 5.4.12 Channels |  | 40 |
|  | 5.4.13 Bye Passes from Various Plant Units |  | 40 |
|  | 5.5 Methodology |  | 42 |
| Chapter 6 | RESULTS AND DISCUSSION |  | 52 |
|  | 6.1 Performance of 16 MGD Okhla STP during winter (December 2004) |  | 52 |
|  | 6.1.1 Raw Sewage Characteristics |  | 52 |
|  | 6.1.2 Primary Effluent |  | 52 |
|  | 6.1.3 Final Effluent |  | 53 |
|  | 6.1.4 Characteristics of the Sludge |  | 53 |
|  | - Performance of 16 MGD Okhla STP during summer (June 2005) |  | 54 |
|  | 6.2.1 Raw Sewage Characteristics |  | 54 |
|  | 6.2.2 Primary Effluent |  | 54 |
|  | 6.2.3 Final Effluent |  | 54 |
|  | 6.2.4 Characteristics of the Sludge |  | 55 |
| Chapter 7 | CONCLUSIONS AND RECOMMENDATIONS |  | 56 |
|  | 7.1 Conclusions |  | 56 |
|  | 7.2 Recommendations |  | 57 |
| Chapter 8 | SUGGESTIONS FOR IMPROVEMENT IN THE EXISTING PLANT |  | 59 |
|  | 8.1 Suggestions for Improvement |  | 59 |
| REFERENCES |  |  | 97 |

List of Tables

| Table | Title | Page No. |
| --- | --- | --- |
| Table-2.1 | Expected efficiencies of various treatment units | 12 |
| Table-4.1 | Sampling locations, parameters and nature of samples for performance evaluation | 28 |
| Table-4.2 | Analytical Methods for Analysis of Sewage Samples | 29 |
| Table-5.1 | Sizes of Units and Details of Components | 41 |
| Table-6.1 | Characteristics of Raw sewage for the month of December 2004 | 61 |
| Table-6.2 | Parameters of Primary treated sewage for the month of December 2004 | 62 |
| Table-6.3 | % Reduction in Suspended Solids in Primary Clarifier for the month of December 2004 | 63 |
| Table-6.4 | % Reduction in B.O.D. in Primary Clarifier for the month of December 2004 | 64 |
| Table-6.5 | % Reduction in C.O.D. in Primary Clarifier for the month of December 2004 | 65 |
| Table-6.6 | Parameters of Mixed Liquor for the month of December 2004 | 69 |
| Table-6.7 | Parameters of Final Effluent for the month of December 2004 | 70 |
| Table-6.8 | % Reduction in Suspended Solids after treatment for the month of December 2004 | 71 |
| Table-6.9 | % Reduction in B. O. D. after treatment for the month of December 2004 | 72 |
| Table-6.10 | % Reduction in C. O. D. after treatment for the month of December 2004 | 73 |
| Table-6.11 | Characteristics of Raw Sludge & Digested Sludge for the month of December 2004 | 77 |
| Table-6.12 | Characteristics of Raw Sewage for the month of June 2005 | 79 |
| Table-6.13 | Parameters of Primary treated sewage for the month of June 2005 | 80 |
| Table-6.14 | % Reduction in Suspended Solids in Primary Clarifier for the month of June 2005 | 81 |
| Table-6.15 | % Reduction in B. O. D. in Primary Clarifier for the month of June 2005 | 82 |
| Table-6.16 | % Reduction in C. O. D. in Primary Clarifier for the month of June 2005 | 83 |
| Table-6.17 | Parameters of Mixed Liquor for the month of June 2005 | 87 |
| Table-6.18 | Parameters of Final Effluent for the month of June 2005 | 88 |
| Table-6.19 | % Reduction in Suspended Solids after treatment for the month of June 2005 | 89 |
| Table | Title | Page No. |
| Table-6.20 | % Reduction in B.O.D. after treatment for the month of June 2005 | 90 |
| Table-6.21 | % Reduction in C.O.D. after treatment for the month of June 2005 | 91 |
| Table-6.22 | Characteristics of Raw Sludge & Digested Sludge for the month of June 2005 | 95 |

List of Figures

| Figure | Title | Page No. |
| --- | --- | --- |
| Fig. 1 | Layout Plan of 16 MGD Sewage Treatment Plant at Okhla, Delhi | 44 |
| Fig. 2 | Hydraulic Flow Diagram of the plant | 45 |
| Fig. 3 | Plan and Section of Primary Clarifier | 46 |
| Fig. 4 | Plan and Section of Aeration Tank | 47 |
| Fig. 5 | Plan and section of Secondary Clarifier | 49 |
| Fig. 6 | Plan and Section of Digester | 50 |
| Fig. 7(a) | Suspended Solids in Raw and Primary treated sewage for the month of December 2004 | 66 |
| Fig. 7(b) | % Reduction in Suspended Solids in Primary Clarifier for the month of December 2004 | 66 |
| Fig. 8(a) | BOD of Raw and Primary treated sewage for the month of December 2004 | 67 |
| Fig. 8(b) | % Reduction in B.O.D. in Primary Clarifier for the month of December 2004 | 67 |
| Fig. 9(a) | COD of Raw and Primary treated sewage for the month of December 2004 | 68 |
| Fig. 9(b) | % Reduction in C.O.D. in Primary Clarifier for the month of December 2004 | 68 |
| Fig. 10(a) | Suspended Solids in Raw and Treated sewage for the month of December 2004 | 74 |
| Fig. 10(b) | % Reduction in Suspended Solids during treatment for the month of December 2004 | 74 |
| Fig. 11(a) | BOD of Raw and Treated sewage for the month of December 2004 | 75 |
| Fig. 11(b) | % Reduction in B. O. D. during treatment for the month of December 2004 | 75 |
| Fig. 12(a) | COD of Raw and Treated sewage for the month of December 2004 | 76 |
| Fig. 12(b) | % Reduction in C. O. D. during treatment for the month of December 2004 | 76 |
| Fig. 13(a) | Volatile matter in Raw Sludge & Digested Sludge for the month of December 2004 | 78 |
| Fig. 13(b) | % Reduction in Volatile Matter during Digestion for the month of December 2004 | 78 |
| Fig. 14(a) | Suspended Solids in Raw and Primary treated sewage for the month of June 2005 | 84 |
| Fig. 14(b) | % Reduction in Suspended Solids in Primary Clarifier for the month of June 2005 | 84 |
| Fig. 15(a) | BOD of Raw and Primary treated sewage for the month of June 2005 | 85 |
| Fig. 15(b) | % Reduction in B.O.D. in Primary Clarifier for the month of June 2005 | 85 |
| Fig. 16(a) | COD of Raw and Primary treated sewage for the month of June 2005 | 86 |
| Fig. 16(b) | % Reduction in C.O.D. in Primary Clarifier for the month of June 2005 | 86 |
| Fig. 17(a) | Suspended Solids in Raw and Treated sewage for the month of June 2005 | 92 |
| Fig. 17(b) | % Reduction in Suspended Solids during treatment for the month of June 2005 | 92 |
| Fig. 18(a) | BOD of Raw and Treated sewage for the month of June 2005 | 93 |
| Fig. 18(b) | % Reduction in B. O. D. during treatment for the month of June 2005 | 93 |
| Fig. 19(a) | COD of Raw and Treated sewage for the month of June 2005 | 94 |
| Fig. 19(b) | % Reduction in C. O. D. during treatment for the month of June 2005 | 94 |
| Fig. 20(a) | Volatile matter in Raw Sludge & Digested Sludge for the month of June 2005 | 96 |
| Fig. 20(b) | % Reduction in Volatile Matter during Digestion for the month of June 2005 | 96 |

List of Pictures

| Picture | Title | Page No. |
| --- | --- | --- |
| Picture-1 | Primary Clarifier | 48 |
| Picture-2 | Aeration Tank | 48 |
| Picture-3 | Secondary Clarifier | 51 |
| Picture-4 | Digester | 51 |

Abbreviations & Acronyms

AS		Activated Sludge

ASP		Activated Sludge Process

BOD		Biochemical Oxygen Demand

BOD5	5 days Biochemical Oxygen Demand

CBOD	Carbonaceous Biochemical Oxygen Demand

bs COD	biodegradable soluble Chemical Oxygen Demand

Cl		Chloride

COD		Chemical Oxygen Demand

CO2		Carbon dioxide

CPHEEO	Central Public Health and Environmental Engineering Organization

H2O		Water

oC		degrees Centigrade

d		day

dia		diametre

DO		Dissolved Oxygen

DS		Dissolve Solids

F:M		Food to Microorganisms ratio

FC		Faecal Coliform

h, hr		hour

HMU	Helixor Mixing Unit

hp		horse power

HRT		Hydraulic Retention Time

IS		Indian Standard

kW		kilo Watt

l, L		Litre

m		metre

mm		millimetre

m2		square metre

m3		cubic metre

MCRT	Mean Cell Residence Time

mg		Milligrams

MGD, mgd	Million Gallons per Day

MLD, mld	Million Litres per Day

MLSS	Mixed Liquor Suspended Solids

MLVSS	Mixed Liquor Volatile Suspended Solids

mm		millimeter

NH3		Ammonia

O&M	Operation and Maintenance

OA		Oxygen Absorption

O2		Oxygen

pH		potential Hydrogen

PO4		Phosphate

RAS		Return Activated Sludge

RBC		Rotating Biological Contactor

RCC		Reinforced Concrete Pipe

RS		Return Sludge

SCADA	Supervisory Control And Data Acquisition

SRT		Sludge Retention Time

SS		Suspended Solids

SST		Secondary Sedimentation Tank

SSV		Settled Sludge Volume

SSVI		Stirred Sludge Volume Index

STP		Sewage Treatment Plant

SVI		Sludge Volume Index

SWD		Side Water Depth

TA		Total Alkalinity

TDS		Total Dissolved Solids

TKN		Total Kjeldahl Nitrogen

TS		Total Solids

TSS		Total Suspended Solids

VA		Voltaic Acid

VOC		Volatile Organic Carbon

VS		Volatile Solids

VSS		Volatile Suspended Solids

WAS		Waste Activated Sludge