CHAPTER-7

CONCLUSIONS AND RECOMMENDATIONS

7.1 CONCLUSIONS

Based on the studies on “performance evaluation study of slaughterhouse waste treatment plant “following conclusions are drawn

- An ETP is installed of capacity 1750cubic meter at Gazipur slaughterhouse to treat the effluent.

- Flow rate of wastewater was observed to be even equal to zero at the night. No pumping station was operating at night.

- Variation   in   characteristics   of samples   of   wastewater collected  for  6 months were  observed  of  the  same  order.  Therefore average   wastewater   characteristic can   be   assumed   to   be   nearly constant throughout.

- The   design   details   provided   by   the   plant   authorities   were compared with the calculated parameters.  It was found that all the parameters were considered while designing.

- The Screens were working satisfactory and screenings are   removed at regular intervals. It was noticed during the visits that the quantity of screening was not much.

- Variation in plant inflow, with   frequent power   interruption   and   low   voltage   resulted   in   the performance of  the various units.

- The gasholder is dome type. The bio- gas produced is flared off in the gas burner fixed at backside.

- All the units from screens to DAF, UASBR to clarifier are working efficiently by giving efficiency of 60-98% at various levels.

- Overall the plant is performing according to the effluent characteristics decided to dispose off.

7.2 RECOMMENDATION

Following recommendations are suggested to improve the performance of the

Slaughterhouse treatment plant:

- Uninterrupted power supply of stable voltage should be ensured for effective O& M of the plant.

- Equal distribution of flow to primary settling tanks, aeration tanks and secondary- settling tanks must ensure to avoid overloading of the units.

- Return  sludge  from  the  secondary  settling  tank  must  be  recycled  to maintain  required  MLSS.

- 1-2 mg/l of DO has to be maintained in aeration tank.

- New operations should be put at the earliest for the proper operation and  for recovery of valuable by product in the form of biogas

- The digester dome (unoperational) should be repaired using anti- corrosive materials and the digester put into operation at the earliest for the proper operation and  for recovery of valuable by product in the form of biogas.

- Necessary training should be imparted to the plant staff particularly at the lower and middle level for effective O & M of the plant.

- Sign board showing  particular  unit  and precautions should  be  placed and maintained from time to time.